## Calc
PUMP HEAD CALCULATION SHEET
Sl.No | Type | Desc | Nos | Length | dia | Discharge | v | Re | e | f | K | Head loss | Cumulative
|  |  |  | m | mm | l/s | m/s
1 | Gravity | Suction head (+ve suction head) |  | -2.1 | [7 empty] | -2.1 | -2.1
2 | Fitting | Entrance | 1 |  | 80 | 19.4 | 3.86 |  |  |  | 0.5 | 0.38 | -1.72
3 | Equipment | Suction strainer |  |  |  | 19.4 | [5 empty] | 1.4 | -0.32
4 | Pipe | Suction line |  | 5 | 80 | 19.4 | 3.86 | 386000 | 0.0015 | 0.0138 |  | 0.656 | 0.336
5 | Pipe | Delivery line |  | 1.5 | 80 | 19.4 | 3.86 | 386000 | 0.0015 | 0.0138 |  | 0.197 | 0.533
6 | Fitting | NRV | 1 |  | 80 | 19.4 | 3.86 |  |  |  | 2.3 | 1.748 | 2.281
7 | Fitting | Butterfly | 1 |  | 80 | 19.4 | 3.86 |  |  |  | 0.4 | 0.304 | 2.585
8 | Pipe | Delivery Header |  | 13 | 200 | 38.8 | 1.24 | 310000 | 0.0015 | 0.0143 |  | 0.073 | 2.658
9 | Pipe | Filter inlet |  | 2.5 | 100 | 38.8 | 4.94 | 617500 | 0.0015 | 0.0127 |  | 0.395 | 3.053
10 | Equipment | Filter |  |  |  | 38.8 | [5 empty] | 8 | 11.053
11 | Pipe | Filter outlet |  | 5 | 100 | 38.8 | 4.94 | 617500 | 0.0015 | 0.0127 |  | 0.791 | 11.844
12 | Pipe | Distribution header |  | 25 | 200 | 38.8 | 1.24 | 310000 | 0.0015 | 0.0143 |  | 0.14 | 11.984
13 | Fitting | NRV | 1 |  | 200 | 38.8 | 1.24 |  |  |  | 12 | 0.941 | 12.925
14 | Pipe | Distribution line |  | 10 | 80 | 9.7 | 1.93 | 193000 | 0.0015 | 0.0158 |  | 0.375 | 13.3
15 | Pipe | Distribution line |  | 5 | 80 | 7.76 | 1.54 | 154000 | 0.0015 | 0.0165 |  | 0.125 | 13.425
16 | Pipe | Distribution line |  | 5 | 80 | 5.82 | 1.16 | 116000 | 0.0015 | 0.0175 |  | 0.075 | 13.5
17 | Pipe | Distribution line |  | 5 | 80 | 3.88 | 0.77 | 77000 | 0.0015 | 0.019 |  | 0.036 | 13.536
18 | Pipe | Distribution line |  | 5 | 80 | 1.94 | 0.39 | 39000 | 0.0015 | 0.022 |  | 0.011 | 13.547
19 | Pipe | Distribution line tee take off |  | 0.7 | 40 | 1.94 | 1.54 | 77000 | 0.0015 | 0.0191 |  | 0.04 | 13.587
20 | Fitting | Exit | 1 |  | 40 | 1.94 | 1.54 |  |  |  | 1 | 0.121 | 13.708
21 | Gravity | Head diff b/w motor and final outlet max |  | 2.2 | [7 empty] | 2.2 | 15.908
|  | Say after 10% safety factor |  | (m) | [8 empty] | 18
|  | Power of motor with 60% pump efficiency, 90% motor efficiency and 20% safety margin |  | (hp) | [8 empty] | 10.2

## e values
PVC | 0.0015
Concrete | 0.3 | 3
GI | 0.15

## kl value
k
Globe valve (fully open) | 6.4
Globe valve (half open) | 9.5
Angle valve (fully open) | 5
Swing check valve (fully open) | 2.5
Butterfly valve (fully open) | 0.4
Gate valve (fully open) | 0.2
Gate valve (3/4 open) | 1
Gate valve (half open) | 5.6
Gate valve (one-quarter open) | 24
Check valve, swing type (fully open) | 2.3
Check valve, lift type (fully open) | 12
Check valve, ball type (fully open) | 70
Foot Valve (fully open) | 15
Close return bend (180º) | 2.2
Standard tee | 1.8
Standard (short radius) elbow (90º) | 0.9
Medium radius elbow (90º) | 0.7
Long sweep elbow (90º) | 0.6
45 degree elbow | 0.4
Pipe entrance (Square-edged) | 0.5
Pipe entrance (Re-entrant) | 0.8
Pipe entrance (Rounded, r/D < 0.16) | 0.1
Pipe exit | 1
Sudden contraction (2 to 1) | 0.25
Sudden contraction (5 to 1) | 0.41
Sudden contraction (10 to 1) | 0.46
Orifice plate (1.5 to 1) | 0.85
Orifice plate (2 to 1) | 3.4
Orifice plate (4 to 1) | 29
Sudden enlargement | (1-A1/A2)2
90 degree miter bend (without vanes) | 1.1
90 degree miter bend (with vanes) | 0.2
General contraction (30 degree included angle) | 0.02
General contraction (70 degree included angle) | 0.07
Tee, Flanged, Dividing Line Flow | 0.2
Tee, Threaded, Dividing Line Flow | 0.9
Tee, Flanged, Dividing Branched Flow | 1
Tee, Threaded , Dividing Branch Flow | 2