## Abs Cooling
COOLING LOAD CALCULATION SHEET
Sl.No | Description | L | B | H | Area | CMH | Cooling coil | Heating coil | # of rows of cooling coil | Static head (supply) | Motor power | Selected CMH for return air blowers | Static head (exhaust) | Motor power
|  | m | m | m | sq.m |  | Tr | kW |  | Pa | hp |  | Pa | hp
100% FRESH AIR (22℃, 50-60% RH) (Pre, Fine, HEPA filters)
A | GROUND FLOOR
| Emergency OT – AHU1 |  |  |  |  | 6800 | 32.415 | 8 | 8 | 1400 | 7.1 | 6120 | 500 | 2.3
B | FIRST FLOOR
| OT1 – AHU2 |  |  |  |  | 8600 | 38.5467 | 7 | 8 | 1400 | 9 | 7740 | 500 | 2.9
| OT3 – AHU3 |  |  |  |  | 8600 | 38.5467 | 7 | 8 | 1400 | 9 | 7740 | 500 | 2.9
| OT3 – AHU4 |  |  |  |  | 8600 | 38.5467 | 7 | 8 | 1400 | 9 | 7740 | 500 | 2.9
[6 empty] | Capacity of hot water generator -> |  | 30 | kW
[6 empty] | After reducing Tr by 30% considering ERW -> | 103.6386
20% RECIRCULATORY AHU (22/24℃, 60% RH) (Pre, Fine filters)
A | FIRST FLOOR
| ICU – AHU5 |  |  |  |  | 13200 | 21.0726 |  | 6 | 1200 | 11.8
| Pediatric – AHU6 |  |  |  |  | 13600 | 21.5056 |  | 6 | 1200 | 12.2
| Labour room – AHU7 |  |  |  |  | 6800 | 10.6429 |  | 6 | 1200 | 6.1 | 1360 | 500 | 0.6
FCUs
|  | L | B | Sqm/TR | Temp |  |  |  | #1.5TR Hiwall | #2TR Hiwall | #3TR FCU
A | GROUND FLOOR
1 | CMO Room | 7 | 3.7 | 15 | 25 |  | 1.8 |  | 2
2 | X-Ray 1 | 6.25 | 5.1 | 5 | 25 |  | 6.4 |  |  | 4
3 | X-Ray 2 | 6.25 | 5.1 | 5 | 25 |  | 6.4 |  |  | 4
4 | Ultrasonic | 6 | 4 | 12 | 25 |  | 2 |  |  | 1
5 | ECG room | 4.3 | 3.4 | 12 | 25 |  | 1.3 |  |  | 1
C | SECOND FLOOR
| MS Room | 7 | 5.3 | 12 | 25 |  | 3.1 |  |  | 2
| Dy MS Room | 7 | 3.5 | 12 | 25 |  | 2.1 |  | 2
| Urinalysis | 4 | 3 | 8 | 24 |  | 1.5 |  | 1
| Bio-chemistry | 5.6 | 2.9 | 8 | 24 |  | 2.1 |  |  |  | 1
| Media room | 5.6 | 3.2 | 8 | 24 |  | 2.3 |  |  |  | 1
| Serology | 5.6 | 3.7 | 8 | 24 |  | 2.6 |  |  |  | 1
| Histology | 5.6 | 3.7 | 8 | 24 |  | 2.6 |  |  |  | 1
| Clinical pathology | 5.6 | 3.7 | 8 | 24 |  | 2.6 |  |  |  | 1
[9 empty] | 5 | 12 | 5
| Connected TR | [5 empty] | 193.6598
| With DF of 80% | [5 empty] | 154.9279
| Add future expansion @ 30% | [5 empty] | 201.4062
[6 empty] | Chiller capacity -> | 3x100 | Tr | (2W+1S)
Note on B28: 22℃ Indoor Air Temperature considered
Note on I11: 3 times calculated value used considering part load operation

## Abs Ventillation
VENTILATION CALCULATION SHEET
Sl.No | Description | L | B | H | Volume | ACH required | Selected CMH for supply air blowers | Static head (supply) | Motor power | Selected CMH for return air blowers | Static head (return) | Motor power | Remarks
|  | m | m | m | cum |  |  | Pa | hp |  | Pa | hp
A | GROUND FLOOR
1 | Canteen
| Exhaust hood | 4.2 | 1 | [6 empty] | 7000.56
[10 empty] | 7000 | 400 | 2.1 | IAD Fan
2 | Kitchen
| Cooking range hood | 6.1 | 1.2 | [6 empty] | 13571.28
| Dosa, chapathi hoods | 4.7 | 1 | [6 empty] | 7833.96
| Steam condensate hood | 3.6 | 1 | [6 empty] | 6000.48
[7 empty] | 27400 | 600 | 12.3 | 27400 | 600 | 12.3 | IAD & FAD Fans
3 | Laundry | 11 | 10 | 4.2 | 462 | 20 |  |  |  | 9300 | 400 | 2.8 | IAD & FAD Fans
3 | Isolation Ward | 7 | 3.5 | 4.2 | 102.9 | 10 |  |  |  | 1100 | 400 | 0.4 | IAD & FAD Fans
A | FIRST FLOOR
1 | CSSD | 10 | 10 | 4.6 | 460 | 25 | 11500 | 900 | 7.8 | 10350 | 400 | 3.1 | Return IAD fan & Supply FAD fan with Pre, Fine filters
2 | Isolation Ward (Maternity) | 7 | 3.2 | 4.6 | 103.04 | 10 |  |  |  | 1100 | 400 | 0.4 | IAD & FAD Fans
3 | Isolation Ward (Surgery) | 7 | 4 | 4.6 | 128.8 | 10 |  |  |  | 1300 | 400 | 0.4 | IAD & FAD Fans
4 | Isolation Room | 3.5 | 2.4 | 4.6 | 38.64 | 10 |  |  |  | 400 | 400 | 0.2 | IAD & FAD Fans
A | SECOND FLOOR
1 | Blood store | 5.6 | 3.2 | 4.2 | 75.26 | 20 |  |  |  | 1600 | 400 | 0.5 | 2# 300Φ industrial exhaust fan

## OT1-Emergency
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Emergency OT | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 22 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 55
HUMIDITY RATIO |  |  | 0.016835 | 0.0090519
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 22
RELATIVE HUMIDITY |  |  | 72 | 60
HUMIDITY RATIO |  |  | 0.022181 | 0.0098748
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  | 28.56 | 2.28 | 15.45 | 1006.0546 | 5.95 | 387.445
2 | EXT. WALL NE |  |  |  |  | 2.28 | 15.85 | 0 | 7.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 15.85 | 0 | 10.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 13.15 | 0 | 12.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 11.95 | 0 | 13.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 13.95 | 0 | 13.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 17.05 | 0 | 12.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 16.65 | 0 | 7.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 85.68 | 2.28 | 12.2 | 2383.2749 | 7.3 | 1426.0579
18 | INT. GLASS. |  |  |  |  | 7.1 | 12.2 | 0 | 7.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 12.2 | 0 | 7.3 | 0
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 31.65 | 0 | 25.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 73.07 | 3.19 | 12.2 | 2843.7383 | 7.3 | 1701.5811
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 6233.0677 |  | 3515.084
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 6 | 6 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.73 | 237 | 0 | 0.73 | 101 | 0 |  | 0.73 | 0.73 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.56 | 625 | 0 | 0.56 | 199 | 0 |  | 0.56 | 0.56 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.47 | 644 | 0 | 0.47 | 675 | 0 |  | 0.47 | 0.47 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.3 | 284 | 0 | 0.3 | 767 | 0 |  | 0.3 | 0.3 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.09 | 126 | 0 | 0.09 | 565 | 0 |  | 0.09 | 0.09 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.07 | 284 | 0 | 0.07 | 767 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.06 | 644 | 0 | 0.06 | 675 | 0 |  | 0.06 | 0.06 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.07 | 625 | 0 | 0.07 | 199 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.12 | 864 | 0 | 0.12 | 820 | 0 |  | 0.12 | 0.12 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 5 | x | 60 | 1 | 300
2 | NO. | 5 | x | 70 |  |  | 350
C | TOTAL BODY GAIN. |  |  |  |  | 300 | 350
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 1 | x | 1000 | 1 | 1 | 1000
6 | AREA LOADING POWER | 1 | x | 5000 | 1 | 1 | 5000
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 6000 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 73.07 | 4.2 | 0 | + |  | 0 | 0 | 0 | 0 | 0
E | TOTAL INFILTRATION GAINS. | [5 empty] | 0 | 0 | 0 | 0
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 6233.0677 | 3515.084 |  | Room S.H.R. (%) |  | 97.28% | 96.56%
2 | SOLAR. |  |  | 0 | 0 |  | No. of Air Changes per hour |  | 18 | 20
3 | BODY |  |  | 300 | 300 |  | TOUT, BAL (OC) |  | -73.7213 | -31.9812
4 | EQUIPMENT |  |  | 6000 | 6000 |  | Solar time used for glass load |  | 6 | 6
5 | INFILTRATION. |  |  | 0 | 0
I | TOTAL ROOM SENSIBLE |  |  | 12533.0677 | 9815.084
1 | BODY |  |  | 350 | 350
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 0 | 0
II | TOTAL ROOM LATENT |  |  | 350 | 350
III | TOTAL ROOM HEAT LOAD |  |  | 12883.0677 | 10165.084
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.0526 | 15
| PRELIMINARY S.A.V. (m3/s) |  |  | 1.1388 | 1.14
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 1400.7519 | 1402.1549
V | FAN GAIN (W) |  |  | 3300 | 3640
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 1.566 | 1.7256
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0089777 | 0.0098074
| MIXING RATIO (% FRESH AIR) |  |  | 1 | 1
| COIL BYPASS FACTOR |  |  | 0.05 | 0.05
| TEMPERATURE OF MIXED AIR (OC) |  |  | 37.2 | 32.3
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.016835 | 0.022181
| WADP OF COOLING COIL |  |  | 0.0085641 | 0.0091562
| TADP OF COOLING COIL (OC) |  |  | 11.7817 | 12.7745
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.0526 | 13.7508
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 46510.98 | 39370.0674
VII | COOLING COIL LATENT LOAD (W) |  |  | 37034.6563 | 64269.6433 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 83545.6363 | 103639.7107
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 23.7548 | 29.4682 | I | COIL LOAD |  | 32.415 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 2.6515 | II | AIR HANDLING CAPACITY |  | 6833.2945 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 5637.4507 | 6212.0859 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 1400 | 1400 |  | CFM/Tr |  | 124
| BLOWER MOTOR I/P (kW) |  |  | 3.3 | 3.64 |  | Sq.m/Tr |  | 2.3
Note on D85: +ve Pressure to be maintained
Note on F103: Temperature required to be reset to acheive minimum 20 ACH requirement

## OT1-3
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, OT 1-3 | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 22 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 56
HUMIDITY RATIO |  |  | 0.016835 | 0.0092165
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 22
RELATIVE HUMIDITY |  |  | 72 | 60
HUMIDITY RATIO |  |  | 0.022181 | 0.0098748
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 15.45 | 0 | 5.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 15.85 | 0 | 7.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 15.85 | 0 | 10.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 13.15 | 0 | 12.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 11.95 | 0 | 13.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 13.95 | 0 | 13.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 17.05 | 0 | 12.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 16.65 | 0 | 7.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 138 | 2.28 | 12.2 | 3838.608 | 7.3 | 2296.872
18 | INT. GLASS. |  |  |  |  | 7.1 | 12.2 | 0 | 7.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  | 81.9 | 3.19 | 12.2 | 3187.3842 | 7.3 | 1907.2053
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 31.65 | 0 | 25.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 81.9 | 3.19 | 12.2 | 3187.3842 | 7.3 | 1907.2053
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 5.05 | 0 | 0.15 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 10213.3764 |  | 6111.2826
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 6 | 6 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.73 | 237 | 0 | 0.73 | 101 | 0 |  | 0.73 | 0.73 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.56 | 625 | 0 | 0.56 | 199 | 0 |  | 0.56 | 0.56 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.47 | 644 | 0 | 0.47 | 675 | 0 |  | 0.47 | 0.47 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.3 | 284 | 0 | 0.3 | 767 | 0 |  | 0.3 | 0.3 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.09 | 126 | 0 | 0.09 | 565 | 0 |  | 0.09 | 0.09 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.07 | 284 | 0 | 0.07 | 767 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.06 | 644 | 0 | 0.06 | 675 | 0 |  | 0.06 | 0.06 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.07 | 625 | 0 | 0.07 | 199 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.12 | 864 | 0 | 0.12 | 820 | 0 |  | 0.12 | 0.12 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 5 | x | 60 | 1 | 300
2 | NO. | 5 | x | 70 |  |  | 350
C | TOTAL BODY GAIN. |  |  |  |  | 300 | 350
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 1 | x | 1000 | 1 | 1 | 1000
6 | AREA LOADING POWER | 1 | x | 5000 | 1 | 1 | 5000
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 6000 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 81.9 | 4.6 | 0 | + |  | 0 | 0 | 0 | 0 | 0
E | TOTAL INFILTRATION GAINS. | [5 empty] | 0 | 0 | 0 | 0
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 10213.3764 | 6111.2826 |  | Room S.H.R. (%) |  | 97.92% | 97.26%
2 | SOLAR. |  |  | 0 | 0 |  | No. of Air Changes per hour |  | 21 | 20
3 | BODY |  |  | 300 | 300 |  | TOUT, BAL (OC) |  | #DIV/0! | #DIV/0!
4 | EQUIPMENT |  |  | 6000 | 6000 |  | Solar time used for glass load |  | 6 | 6
5 | INFILTRATION. |  |  | 0 | 0
I | TOTAL ROOM SENSIBLE |  |  | 16513.3764 | 12411.2826
1 | BODY |  |  | 350 | 350
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 0 | 0
II | TOTAL ROOM LATENT |  |  | 350 | 350
III | TOTAL ROOM HEAT LOAD |  |  | 16863.3764 | 12761.2826
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.3714 | 14.7
| PRELIMINARY S.A.V. (m3/s) |  |  | 1.5559 | 1.3823
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 1913.8019 | 1700.1757
V | FAN GAIN (W) |  |  | 4570 | 4330
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 2.1669 | 2.0538
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0091628 | 0.0098182
| MIXING RATIO (% FRESH AIR) |  |  | 1 | 1
| COIL BYPASS FACTOR |  |  | 0.05 | 0.05
| TEMPERATURE OF MIXED AIR (OC) |  |  | 37.2 | 32.3
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.016835 | 0.022181
| WADP OF COOLING COIL |  |  | 0.0087591 | 0.0091675
| TADP OF COOLING COIL (OC) |  |  | 12.1173 | 12.793
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.3714 | 13.7684
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 63508.7642 | 46815.0381
VII | COOLING COIL LATENT LOAD (W) |  |  | 50038.1011 | 76429.3299 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 113546.8653 | 123244.368
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 32.2851 | 35.0425 | I | COIL LOAD |  | 38.5467 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 2.3534 | II | AIR HANDLING CAPACITY |  | 8580.7595 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 7800.6905 | 7393.8356 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 1400 | 1400 |  | CFM/Tr |  | 131
| BLOWER MOTOR I/P (kW) |  |  | 4.57 | 4.33 |  | Sq.m/Tr |  | 2.1
Note on D85: +ve Pressure to be maintained
Note on F103: Temperature required to be reset to acheive minimum 20 ACH requirement

## ICU
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, ICU | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 24 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 50
HUMIDITY RATIO |  |  | 0.016835 | 0.0093206
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 24
RELATIVE HUMIDITY |  |  | 72 | 51
HUMIDITY RATIO |  |  | 0.022181 | 0.009507
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 13.45 | 0 | 3.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 13.85 | 0 | 5.05 | 0
3 | EXT. WALL E |  |  |  | 58.88 | 2.28 | 13.85 | 1859.3126 | 8.95 | 1201.5053
4 | EXT. WALL SE |  |  |  |  | 2.28 | 11.15 | 0 | 10.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 9.95 | 0 | 11.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 11.95 | 0 | 11.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 15.05 | 0 | 10.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 14.65 | 0 | 5.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  | 17.664 | 5.23 | 4.15 | 383.3883 | -0.75 | -69.287 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 171.58 | 2.28 | 10.2 | 3990.2645 | 5.3 | 2073.3727
18 | INT. GLASS. |  |  |  |  | 7.1 | 10.2 | 0 | 5.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  | 151.9 | 3.19 | 10.2 | 4942.5222 | 5.3 | 2568.1733
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 29.65 | 0 | 23.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 151.9 | 3.19 | 10.2 | 4942.5222 | 5.3 | 2568.1733
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 16118.0098 |  | 8341.9376
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 8 | 8 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.65 | 237 | 0 | 0.65 | 101 | 0 |  | 0.65 | 0.65 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.74 | 625 | 0 | 0.74 | 199 | 0 |  | 0.74 | 0.74 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 17.664 | 0.7 | 0.8 | 644 | 6370.345 | 0.8 | 675 | 6676.992 |  | 0.8 | 0.8 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.74 | 284 | 0 | 0.74 | 767 | 0 |  | 0.74 | 0.74 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.23 | 126 | 0 | 0.23 | 565 | 0 |  | 0.23 | 0.23 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.14 | 284 | 0 | 0.14 | 767 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.11 | 644 | 0 | 0.11 | 675 | 0 |  | 0.11 | 0.11 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.14 | 625 | 0 | 0.14 | 199 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.44 | 864 | 0 | 0.44 | 820 | 0 |  | 0.44 | 0.44 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 6370.345 |  | 3742.5777 | 5733.3105 | 6370.345 | 6051.8277 | 4937.0173 | 3264.8018 | 2149.9914 | 2070.3621 | 1911.1035 | 1751.8449 | 1592.5862 | 1274.069 | 955.5517
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 6370.345 |  |  | 6676.992 |  |  | 6676.992 | 3922.7328 | 6009.2928 | 6676.992 | 6343.1424 | 5174.6688 | 3421.9584 | 2253.4848 | 2170.0224 | 2003.0976 | 1836.1728 | 1669.248 | 1335.3984 | 1001.5488
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 12 | x | 60 | 1 | 720
2 | NO. | 12 | x | 70 |  |  | 840
C | TOTAL BODY GAIN. |  |  |  |  | 720 | 840
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 5 | x | 151.9 | 1 | 1 | 759.5
6 | AREA LOADING POWER | 50 | x | 151.9 | 1 | 1 | 7595
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 8354.5 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 151.9 | 4.6 | 0 | + |  | 0 | 0 | 0 | 0 | 0
E | TOTAL INFILTRATION GAINS. | [5 empty] | 0 | 0 | 0 | 0
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 16118.0098 | 8341.9376 |  | Room S.H.R. (%) |  | 97.41% | 96.63%
2 | SOLAR. |  |  | 6370.345 | 6676.992 |  | No. of Air Changes per hour |  | 17 | 13
3 | BODY |  |  | 720 | 720 |  | TOUT, BAL (OC) |  | -75.2298 | -42.271
4 | EQUIPMENT |  |  | 8354.5 | 8354.5 |  | Solar time used for glass load |  | 8 | 8
5 | INFILTRATION. |  |  | 0 | 0
I | TOTAL ROOM SENSIBLE |  |  | 31562.8548 | 24093.4296
1 | BODY |  |  | 840 | 840
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 0 | 0
II | TOTAL ROOM LATENT |  |  | 840 | 840
III | TOTAL ROOM HEAT LOAD |  |  | 32402.8548 | 24933.4296
| ROOM SUPPLY AIR TEMP (OC) |  |  | 14.0293 | 13.9915
| PRELIMINARY S.A.V. (m3/s) |  |  | 2.5736 | 1.9571
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 3165.5709 | 2407.2853
V | FAN GAIN (W) |  |  | 6000 | 4560
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 3.321 | 2.5231
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0092366 | 0.0093964
| MIXING RATIO (% FRESH AIR) |  |  | 0.2 | 0.2
| COIL BYPASS FACTOR |  |  | 0.1 | 0.1
| TEMPERATURE OF MIXED AIR (OC) |  |  | 26.64 | 25.66
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.010823 | 0.012042
| WADP OF COOLING COIL |  |  | 0.0090603 | 0.0091025
| TADP OF COOLING COIL (OC) |  |  | 12.6281 | 12.6949
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 14.0293 | 13.9915
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 51512.3621 | 36212.3899
VII | COOLING COIL LATENT LOAD (W) |  |  | 15862.5476 | 20091.02 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 67374.9097 | 56303.4099
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 19.1569 | 16.0089 | I | COIL LOAD |  | 21.0726 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 13151.142 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 11955.5836 | 9083.1768 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 1200 | 1200 |  | CFM/Tr |  | 367
| BLOWER MOTOR I/P (kW) |  |  | 6 | 4.56 |  | Sq.m/Tr |  | 7.2
Note on D85: +ve Pressure to be maintained

## Pediatric
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Pediatric Unit | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 24 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 50
HUMIDITY RATIO |  |  | 0.016835 | 0.0093206
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 24
RELATIVE HUMIDITY |  |  | 72 | 50
HUMIDITY RATIO |  |  | 0.022181 | 0.0093206
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 13.45 | 0 | 3.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 13.85 | 0 | 5.05 | 0
3 | EXT. WALL E |  |  |  | 69 | 2.28 | 13.85 | 2178.882 | 8.95 | 1408.014
4 | EXT. WALL SE |  |  |  |  | 2.28 | 11.15 | 0 | 10.55 | 0
5 | EXT. WALL S |  |  |  | 16.1 | 2.28 | 9.95 | 365.2446 | 11.65 | 427.6482
6 | EXT. WALL SW |  |  |  |  | 2.28 | 11.95 | 0 | 11.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 15.05 | 0 | 10.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 14.65 | 0 | 5.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  | 20.7 | 5.23 | 4.15 | 449.2832 | -0.75 | -81.1958 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  | 4.83 | 5.23 | 4.15 | 104.8327 | -0.75 | -18.9457 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 209.3 | 2.28 | 10.2 | 4867.4808 | 5.3 | 2529.1812
18 | INT. GLASS. |  |  |  |  | 7.1 | 10.2 | 0 | 5.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  | 155 | 3.19 | 10.2 | 5043.39 | 5.3 | 2620.585
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 29.65 | 0 | 23.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 155 | 3.19 | 10.2 | 5043.39 | 5.3 | 2620.585
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 18052.5033 |  | 9505.872
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 8 | 8 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.65 | 237 | 0 | 0.65 | 101 | 0 |  | 0.65 | 0.65 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.74 | 625 | 0 | 0.74 | 199 | 0 |  | 0.74 | 0.74 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 20.7 | 0.7 | 0.8 | 644 | 7465.248 | 0.8 | 675 | 7824.6 |  | 0.8 | 0.8 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.74 | 284 | 0 | 0.74 | 767 | 0 |  | 0.74 | 0.74 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 4.83 | 0.7 | 0.23 | 126 | 97.9814 | 0.23 | 565 | 439.361 |  | 0.23 | 0.23 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.14 | 284 | 0 | 0.14 | 767 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.11 | 644 | 0 | 0.11 | 675 | 0 |  | 0.11 | 0.11 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.14 | 625 | 0 | 0.14 | 199 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.44 | 864 | 0 | 0.44 | 820 | 0 |  | 0.44 | 0.44 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 7563.2294 |  | 4424.1737 | 6786.8842 | 7563.2294 | 7253.8679 | 6032.6507 | 4145.4441 | 2873.1062 | 2767.0104 | 2529.2585 | 2265.9462 | 2015.4141 | 1608.0712 | 1200.7283
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 7563.2294 |  |  | 8263.961 |  |  | 8263.961 | 4768.8763 | 7347.7824 | 8263.961 | 8159.2707 | 7172.0187 | 5442.8062 | 4226.3224 | 4071.207 | 3646.3602 | 3106.8975 | 2624.7427 | 2080.6916 | 1536.6403
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 5 | x | 60 | 1 | 300
2 | NO. | 5 | x | 70 |  |  | 350
C | TOTAL BODY GAIN. |  |  |  |  | 300 | 350
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 5 | x | 155 | 1 | 1 | 775
6 | AREA LOADING POWER | 30 | x | 155 | 1 | 1 | 4650
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 5425 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 155 | 4.6 | 0 | + |  | 0 | 0 | 0 | 0 | 0
E | TOTAL INFILTRATION GAINS. | [5 empty] | 0 | 0 | 0 | 0
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 18052.5033 | 9505.872 |  | Room S.H.R. (%) |  | 98.9% | 98.53%
2 | SOLAR. |  |  | 7563.2294 | 8263.961 |  | No. of Air Changes per hour |  | 17 | 13
3 | BODY |  |  | 300 | 300 |  | TOUT, BAL (OC) |  | -54.2041 | -30.2508
4 | EQUIPMENT |  |  | 5425 | 5425 |  | Solar time used for glass load |  | 8 | 8
5 | INFILTRATION. |  |  | 0 | 0
I | TOTAL ROOM SENSIBLE |  |  | 31340.7327 | 23494.8329
1 | BODY |  |  | 350 | 350
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 0 | 0
II | TOTAL ROOM LATENT |  |  | 350 | 350
III | TOTAL ROOM HEAT LOAD |  |  | 31690.7327 | 23844.8329
| ROOM SUPPLY AIR TEMP (OC) |  |  | 14.1121 | 13.8129
| PRELIMINARY S.A.V. (m3/s) |  |  | 2.5769 | 1.8751
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 3169.6099 | 2306.339
V | FAN GAIN (W) |  |  | 7230 | 5220
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 3.432 | 2.4757
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0092867 | 0.0092737
| MIXING RATIO (% FRESH AIR) |  |  | 0.2 | 0.2
| COIL BYPASS FACTOR |  |  | 0.1 | 0.1
| TEMPERATURE OF MIXED AIR (OC) |  |  | 26.64 | 25.66
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.010823 | 0.011893
| WADP OF COOLING COIL |  |  | 0.009116 | 0.0089826
| TADP OF COOLING COIL (OC) |  |  | 12.7201 | 12.4966
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 14.1121 | 13.8129
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 52884.7402 | 36076.1245
VII | COOLING COIL LATENT LOAD (W) |  |  | 15874.6876 | 19517.4101 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 68759.4279 | 55593.5345
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 19.5506 | 15.8071 | I | COIL LOAD |  | 21.5056 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 13590.7289 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 12355.2081 | 8912.6403 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 1400 | 1400 |  | CFM/Tr |  | 372
| BLOWER MOTOR I/P (kW) |  |  | 7.23 | 5.22 |  | Sq.m/Tr |  | 7.2
Note on D85: +ve Pressure to be maintained

## Labour room
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Labour Room | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 22 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 58
HUMIDITY RATIO |  |  | 0.016835 | 0.0095457
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 22
RELATIVE HUMIDITY |  |  | 72 | 60
HUMIDITY RATIO |  |  | 0.022181 | 0.0098748
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 15.45 | 0 | 5.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 15.85 | 0 | 7.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 15.85 | 0 | 10.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 13.15 | 0 | 12.55 | 0
5 | EXT. WALL S |  |  |  | 36.8 | 2.28 | 11.95 | 1002.6528 | 13.65 | 1145.2896
6 | EXT. WALL SW |  |  |  |  | 2.28 | 13.95 | 0 | 13.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 17.05 | 0 | 12.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 16.65 | 0 | 7.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  | 11.04 | 5.23 | 11.15 | 643.7921 | 6.25 | 360.87 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 100.28 | 2.28 | 12.2 | 2789.3885 | 7.3 | 1669.0603
18 | INT. GLASS. |  |  |  |  | 7.1 | 12.2 | 0 | 7.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  | 55.2 | 3.19 | 12.2 | 2148.2736 | 7.3 | 1285.4424
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 31.65 | 0 | 25.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 55.2 | 3.19 | 12.2 | 2148.2736 | 7.3 | 1285.4424
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 11.15 | 0 | 6.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 8732.3806 |  | 5746.1047
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 12 | 12 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.89 | 237 | 0 | 0.89 | 101 | 0 |  | 0.89 | 0.89 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.27 | 625 | 0 | 0.27 | 199 | 0 |  | 0.27 | 0.27 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.27 | 644 | 0 | 0.27 | 675 | 0 |  | 0.27 | 0.27 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.49 | 284 | 0 | 0.49 | 767 | 0 |  | 0.49 | 0.49 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 11.04 | 0.7 | 0.83 | 126 | 808.1942 | 0.83 | 565 | 3624.0456 |  | 0.83 | 0.83 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.38 | 284 | 0 | 0.38 | 767 | 0 |  | 0.38 | 0.38 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.17 | 644 | 0 | 0.17 | 675 | 0 |  | 0.17 | 0.17 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.21 | 625 | 0 | 0.21 | 199 | 0 |  | 0.21 | 0.21 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.85 | 864 | 0 | 0.85 | 820 | 0 |  | 0.85 | 0.85 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 808.1942 |  | 87.6355 | 155.7965 | 223.9574 | 370.0166 | 564.7622 | 730.296 | 808.1942 | 778.9824 | 662.135 | 486.864 | 340.8048 | 262.9066 | 185.0083
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 808.1942 |  |  | 3624.0456 |  |  | 3624.0456 | 392.9688 | 698.6112 | 1004.2536 | 1659.2016 | 2532.4656 | 3274.74 | 3624.0456 | 3493.056 | 2969.0976 | 2183.16 | 1528.212 | 1178.9064 | 829.6008
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 8 | x | 60 | 1 | 480
2 | NO. | 8 | x | 70 |  |  | 560
C | TOTAL BODY GAIN. |  |  |  |  | 480 | 560
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 5 | x | 55.2 | 1 | 1 | 276
6 | AREA LOADING POWER | 30 | x | 55.2 | 1 | 1 | 1656
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 1932 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 55.2 | 4.6 | 0.5 | + |  | 126.96 | 659.3456 | 773.7565 | 446.7934 | 1306.3628
E | TOTAL INFILTRATION GAINS. | [5 empty] | 659.3456 | 773.7565 | 446.7934 | 1306.3628
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 8732.3806 | 5746.1047 |  | Room S.H.R. (%) |  | 90.44% | 86.76%
2 | SOLAR. |  |  | 808.1942 | 3624.0456 |  | No. of Air Changes per hour |  | 24 | 23
3 | BODY |  |  | 480 | 480 |  | TOUT, BAL (OC) |  | -45.3564 | -44.1532
4 | EQUIPMENT |  |  | 1932 | 1932 |  | Solar time used for glass load |  | 12 | 12
5 | INFILTRATION. |  |  | 659.3456 | 446.7934
I | TOTAL ROOM SENSIBLE |  |  | 12611.9204 | 12228.9437
1 | BODY |  |  | 560 | 560
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 773.7565 | 1306.3628
II | TOTAL ROOM LATENT |  |  | 1333.7565 | 1866.3628
III | TOTAL ROOM HEAT LOAD |  |  | 13945.6769 | 14095.3065
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.9242 | 13.9251
| PRELIMINARY S.A.V. (m3/s) |  |  | 1.2697 | 1.2312
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 1561.6854 | 1514.4347
V | FAN GAIN (W) |  |  | 2960 | 2310
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 1.7249 | 1.6163
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.009288 | 0.0094832
| MIXING RATIO (% FRESH AIR) |  |  | 0.2 | 0.2
| COIL BYPASS FACTOR |  |  | 0.1 | 0.1
| TEMPERATURE OF MIXED AIR (OC) |  |  | 25.04 | 24.06
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.011003 | 0.012336
| WADP OF COOLING COIL |  |  | 0.0090974 | 0.0091662
| TADP OF COOLING COIL (OC) |  |  | 12.6891 | 12.799
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.9242 | 13.9251
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 23583.2342 | 20148.7686
VII | COOLING COIL LATENT LOAD (W) |  |  | 8906.4508 | 13879.5549 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 32489.685 | 34028.3235
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 9.2379 | 9.6754 | I | COIL LOAD |  | 10.6429 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 6830.4793 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 6209.5267 | 5818.6931 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 1200 | 1200 |  | CFM/Tr |  | 378
| BLOWER MOTOR I/P (kW) |  |  | 2.96 | 2.31 |  | Sq.m/Tr |  | 5.2

## VALUES
DATA FOR CHENNAI/PUDUCHERRY
I | SHGF FACTORS FOR GLASS
|  | SUMMER |  | RAINY
| DIRECTION | SHGF FOR 12°N & JUNE | SHGC | SHGF FOR 8°N & NOV | SHGC
|  | Btu/(hr.ft^2) | W/m2 | Btu/(hr.ft^2) | W/m2
| N | 75 | 237 | 32 | 101
| NE | 198 | 625 | 63 | 199
| E | 204 | 644 | 214 | 675
| SE | 90 | 284 | 243 | 767
| S | 40 | 126 | 179 | 565
| SW | 90 | 284 | 243 | 767
| W | 204 | 644 | 214 | 675
| NW | 198 | 625 | 63 | 199
| HORIZONTAL | 274 | 864 | 260 | 820
I | CLF FACTORS FOR GLASS
| DIRECTION | SOLAR TIME
|  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| N | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
| NE | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
| E | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
| SE | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
| S | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
| SW | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
| W | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
| NW | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
| HORIZONTAL | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
II | CLTD FACTORS FOR ROOF
|  |  | SUMMER |  |  | RAINY
| DIRECTION | SOLAR TIME 6: CLTD FOR ROOF (4" CC with insulation); SOLAR TIME 7: CORRECTION FOR 8°N & JUNE; SOLAR TIME 8: COLOUR CORRECTION; SOLAR TIME 9: CLTD FOR ROOF; SOLAR TIME 10: CORRECTION FOR 8°N & NOV; SOLAR TIME 11: COLOUR CORRECTION; SOLAR TIME 12: CLTD FOR ROOF
|  | °F | °F |  | °C | °F |  | °C
| HORIZONTAL | SOLAR TIME 6: 53; SOLAR TIME 7: -2; SOLAR TIME 8: 0.9; SOLAR TIME 9: 25.5; SOLAR TIME 10: -4; SOLAR TIME 11: 0.9; SOLAR TIME 12: 24.5
III | CLTD FACTORS FOR WALL
|  |  | SUMMER |  |  | RAINY
| DIRECTION | SOLAR TIME 6: CLTD FOR WALL (8" BRICK); SOLAR TIME 7: CORRECTION FOR 8°N & JUNE; SOLAR TIME 8: COLOUR CORRECTION; SOLAR TIME 9: CLTD FOR WALL; SOLAR TIME 10: CORRECTION FOR 8°N & NOV; SOLAR TIME 11: COLOUR CORRECTION; SOLAR TIME 12: CLTD FOR WALL
|  | °F | °F |  | °C | °F |  | °C
| N | SOLAR TIME 6: 15; SOLAR TIME 7: 9; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.3; SOLAR TIME 10: -3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 4.7
| NE | SOLAR TIME 6: 21; SOLAR TIME 7: 4; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.7; SOLAR TIME 10: -6; SOLAR TIME 11: 0.7; SOLAR TIME 12: 5.8
| E | SOLAR TIME 6: 27; SOLAR TIME 7: -2; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.7; SOLAR TIME 10: -2; SOLAR TIME 11: 0.7; SOLAR TIME 12: 9.7
| SE | SOLAR TIME 6: 26; SOLAR TIME 7: -8; SOLAR TIME 8: 0.7; SOLAR TIME 9: 7; SOLAR TIME 10: 3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 11.3
| S | SOLAR TIME 6: 22; SOLAR TIME 7: -7; SOLAR TIME 8: 0.7; SOLAR TIME 9: 5.8; SOLAR TIME 10: 10; SOLAR TIME 11: 0.7; SOLAR TIME 12: 12.4
| SW | SOLAR TIME 6: 28; SOLAR TIME 7: -8; SOLAR TIME 8: 0.7; SOLAR TIME 9: 7.8; SOLAR TIME 10: 3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 12.1
| W | SOLAR TIME 6: 30; SOLAR TIME 7: -2; SOLAR TIME 8: 0.7; SOLAR TIME 9: 10.9; SOLAR TIME 10: -2; SOLAR TIME 11: 0.7; SOLAR TIME 12: 10.9
| NW | SOLAR TIME 6: 23; SOLAR TIME 7: 4; SOLAR TIME 8: 0.7; SOLAR TIME 9: 10.5; SOLAR TIME 10: -6; SOLAR TIME 11: 0.7; SOLAR TIME 12: 6.6
IV | CLTD FACTORS FOR GLASS
| DIRECTION | SOLAR TIME 6: SOLAR TIME
|  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| ALL (°F) | -2 | -2 | 0 | 2 | 4 | 7 | 9 | 12 | 13 | 14 | 14 | 13 | 12
| ALL (°C) | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
V | TYPICAL VALUES
ACTIVITY LEVEL
| Degree of Activity | SOLAR TIME 6: Typical Application; SOLAR TIME 7: Average Metabolic Rate - male adult (W); SOLAR TIME 8: Room Dry Bulb Temperature (oC)
|  |  |  | 28 |  | 27 |  | 26 |  | 24 |  | 22 |  | 20
Heat (W)
|  |  |  | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat.
| Seated at rest | Cinema, theater, school | 100 | 50 | 50 | 55 | 45 | 60 | 40 | 67 | 33 | 72 | 28 | 79 | 21
| Seated, very light work | Computer working | 120 | 50 | 70 | 55 | 65 | 60 | 60 | 70 | 50 | 78 | 42 | 84 | 36
| Office work | Hotel reception, cashier | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
| Standing, walking slowly | Laboratory work | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
| Walking, seated |  | 150 | 53 | 97 | 58 | 92 | 64 | 86 | 76 | 74 | 84 | 66 | 90 | 60
| Moderate work | Servant, hair dresser | 160 | 55 | 105 | 60 | 100 | 68 | 92 | 80 | 80 | 90 | 70 | 98 | 62
| Light bench work | Mechanical production | 220 | 55 | 165 | 52 | 158 | 70 | 150 | 85 | 135 | 100 | 120 | 115 | 105
| Moderate Dancing | Party | 250 | 62 | 188 | 70 | 180 | 78 | 172 | 94 | 156 | 110 | 140 | 125 | 125
| Fast walking | Mountain walking | 300 | 80 | 220 | 88 | 212 | 96 | 204 | 110 | 190 | 130 | 170 | 145 | 155
| Heavy work | Athletics | 430 | 132 | 298 | 138 | 292 | 144 | 286 | 154 | 276 | 170 | 260 | 188 | 242

## CMO room
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Pediatric Unit | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 25 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 47
HUMIDITY RATIO |  |  | 0.016835 | 0.0093193
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 25
RELATIVE HUMIDITY |  |  | 72 | 50
HUMIDITY RATIO |  |  | 0.022181 | 0.0099142
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 12.45 | 0 | 2.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 12.85 | 0 | 4.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 12.85 | 0 | 7.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 10.15 | 0 | 9.55 | 0
5 | EXT. WALL S |  |  |  | 15.54 | 2.28 | 8.95 | 317.1092 | 10.65 | 377.3423
6 | EXT. WALL SW |  |  |  |  | 2.28 | 10.95 | 0 | 10.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 14.05 | 0 | 9.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 13.65 | 0 | 4.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  | 4.662 | 5.23 | 8.15 | 198.7154 | 3.25 | 79.2423 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 74.34 | 2.28 | 9.2 | 1559.3558 | 4.3 | 728.8294
18 | INT. GLASS. |  |  |  |  | 7.1 | 9.2 | 0 | 4.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 9.2 | 0 | 4.3 | 0
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 28.65 | 0 | 22.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 25.9 | 3.19 | 9.2 | 760.1132 | 4.3 | 355.2703
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 8.15 | 0 | 3.25 | 0 |  | 5 | 5 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 2835.2937 |  | 1540.6843
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 12 | 12 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.89 | 237 | 0 | 0.89 | 101 | 0 |  | 0.89 | 0.89 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.27 | 625 | 0 | 0.27 | 199 | 0 |  | 0.27 | 0.27 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.27 | 644 | 0 | 0.27 | 675 | 0 |  | 0.27 | 0.27 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.49 | 284 | 0 | 0.49 | 767 | 0 |  | 0.49 | 0.49 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 4.662 | 0.7 | 0.83 | 126 | 341.2864 | 0.83 | 565 | 1530.3714 |  | 0.83 | 0.83 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.38 | 284 | 0 | 0.38 | 767 | 0 |  | 0.38 | 0.38 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.17 | 644 | 0 | 0.17 | 675 | 0 |  | 0.17 | 0.17 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.21 | 625 | 0 | 0.21 | 199 | 0 |  | 0.21 | 0.21 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.85 | 864 | 0 | 0.85 | 820 | 0 |  | 0.85 | 0.85 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 341.2864 |  | 37.007 | 65.7901 | 94.5733 | 156.2516 | 238.4893 | 308.3913 | 341.2864 | 328.9507 | 279.6081 | 205.5942 | 143.9159 | 111.0209 | 78.1258
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 341.2864 |  |  | 1530.3714 |  |  | 1530.3714 | 165.9439 | 295.0114 | 424.0788 | 700.652 | 1069.4162 | 1382.8657 | 1530.3714 | 1475.0568 | 1253.7983 | 921.9105 | 645.3374 | 497.8317 | 350.326
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 3 | x | 60 | 1 | 180
2 | NO. | 3 | x | 70 |  |  | 210
C | TOTAL BODY GAIN. |  |  |  |  | 180 | 210
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 3 | x | 25.9 | 1 | 1 | 77.7
6 | AREA LOADING POWER | 10 | x | 25.9 | 1 | 1 | 259
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 336.7 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 25.9 | 4.2 | 1 | + |  | 108.78 | 453.4313 | 683.5464 | 271.3154 | 1115.7213
E | TOTAL INFILTRATION GAINS. | [5 empty] | 453.4313 | 683.5464 | 271.3154 | 1115.7213
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 2835.2937 | 1540.6843 |  | Room S.H.R. (%) |  | 82.27% | 74.43%
2 | SOLAR. |  |  | 341.2864 | 1530.3714 |  | No. of Air Changes per hour |  | 11 | 11
3 | BODY |  |  | 180 | 180 |  | TOUT, BAL (OC) |  | -28.1081 | -26.3439
4 | EQUIPMENT |  |  | 336.7 | 336.7 |  | Solar time used for glass load |  | 12 | 12
5 | INFILTRATION. |  |  | 453.4313 | 271.3154
I | TOTAL ROOM SENSIBLE |  |  | 4146.7114 | 3859.0712
1 | BODY |  |  | 210 | 210
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 683.5464 | 1115.7213
II | TOTAL ROOM LATENT |  |  | 893.5464 | 1325.7213
III | TOTAL ROOM HEAT LOAD |  |  | 5040.2577 | 5184.7925
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.9779 | 13.8926
| PRELIMINARY S.A.V. (m3/s) |  |  | 0.30587 | 0.28247
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 376.2195 | 347.4331
V | FAN GAIN (W) |  |  | 160 | 150
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 0.34542 | 0.31888
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0084599 | 0.0085329
| MIXING RATIO (% FRESH AIR) |  |  | 0 | 0
| COIL BYPASS FACTOR |  |  | 0.2 | 0.2
| TEMPERATURE OF MIXED AIR (OC) |  |  | 25 | 25
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.0093193 | 0.0099142
| WADP OF COOLING COIL |  |  | 0.008245 | 0.0081876
| TADP OF COOLING COIL (OC) |  |  | 11.2224 | 11.1158
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.9779 | 13.8926
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 4682.9309 | 4356.5043
VII | COOLING COIL LATENT LOAD (W) |  |  | 893.5464 | 1325.7213 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 5576.4773 | 5682.2256
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 1.5856 | 1.6156 | I | COIL LOAD |  | 1.7772 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 1367.8716 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 1243.5197 | 1147.9526 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 300 | 300 |  | CFM/Tr |  | 453
| BLOWER MOTOR I/P (kW) |  |  | 0.16 | 0.15 |  | Sq.m/Tr |  | 14.6

## Clinical Pathology
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Pediatric Unit | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 24 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 48
HUMIDITY RATIO |  |  | 0.016835 | 0.0089478
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 24
RELATIVE HUMIDITY |  |  | 72 | 51
HUMIDITY RATIO |  |  | 0.022181 | 0.009507
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 13.45 | 0 | 3.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 13.85 | 0 | 5.05 | 0
3 | EXT. WALL E |  |  |  | 15.54 | 2.28 | 13.85 | 490.7221 | 8.95 | 317.1092
4 | EXT. WALL SE |  |  |  |  | 2.28 | 11.15 | 0 | 10.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 9.95 | 0 | 11.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 11.95 | 0 | 11.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 15.05 | 0 | 10.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 14.65 | 0 | 5.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  | 4.662 | 5.23 | 4.15 | 101.1864 | -0.75 | -18.2867 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 54.6 | 2.28 | 10.2 | 1269.7776 | 5.3 | 659.7864
18 | INT. GLASS. |  |  |  |  | 7.1 | 10.2 | 0 | 5.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 10.2 | 0 | 5.3 | 0
20 | ROOF EXPOSED |  |  |  | 20.72 | 0.7 | 29.65 | 430.0436 | 23.75 | 344.47
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 20.72 | 3.19 | 10.2 | 674.1874 | 5.3 | 350.313
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 4.15 | 0 | -0.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 2965.9171 |  | 1653.392
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 8 | 8 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.65 | 237 | 0 | 0.65 | 101 | 0 |  | 0.65 | 0.65 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.74 | 625 | 0 | 0.74 | 199 | 0 |  | 0.74 | 0.74 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 4.662 | 0.7 | 0.8 | 644 | 1681.3037 | 0.8 | 675 | 1762.236 |  | 0.8 | 0.8 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.74 | 284 | 0 | 0.74 | 767 | 0 |  | 0.74 | 0.74 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.23 | 126 | 0 | 0.23 | 565 | 0 |  | 0.23 | 0.23 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.14 | 284 | 0 | 0.14 | 767 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.11 | 644 | 0 | 0.11 | 675 | 0 |  | 0.11 | 0.11 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.14 | 625 | 0 | 0.14 | 199 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.44 | 864 | 0 | 0.44 | 820 | 0 |  | 0.44 | 0.44 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 1681.3037 |  | 987.7659 | 1513.1733 | 1681.3037 | 1597.2385 | 1303.0104 | 861.6681 | 567.44 | 546.4237 | 504.3911 | 462.3585 | 420.3259 | 336.2607 | 252.1956
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 1681.3037 |  |  | 1762.236 |  |  | 1762.236 | 1035.3137 | 1586.0124 | 1762.236 | 1674.1242 | 1365.7329 | 903.1459 | 594.7546 | 572.7267 | 528.6708 | 484.6149 | 440.559 | 352.4472 | 264.3354
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 3 | x | 60 | 1 | 180
2 | NO. | 3 | x | 70 |  |  | 210
C | TOTAL BODY GAIN. |  |  |  |  | 180 | 210
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 5 | x | 20.72 | 1 | 1 | 103.6
6 | AREA LOADING POWER | 30 | x | 20.72 | 1 | 1 | 621.6
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 725.2 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 20.72 | 4.2 | 1 | + |  | 87.024 | 392.4782 | 573.8687 | 246.7856 | 922.1998
E | TOTAL INFILTRATION GAINS. | [5 empty] | 392.4782 | 573.8687 | 246.7856 | 922.1998
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 2965.9171 | 1653.392 |  | Room S.H.R. (%) |  | 88.35% | 80.14%
2 | SOLAR. |  |  | 1681.3037 | 1762.236 |  | No. of Air Changes per hour |  | 23 | 18
3 | BODY |  |  | 180 | 180 |  | TOUT, BAL (OC) |  | -38.532 | -21.96
4 | EQUIPMENT |  |  | 725.2 | 725.2 |  | Solar time used for glass load |  | 8 | 8
5 | INFILTRATION. |  |  | 392.4782 | 246.7856
I | TOTAL ROOM SENSIBLE |  |  | 5944.899 | 4567.6135
1 | BODY |  |  | 210 | 210
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 573.8687 | 922.1998
II | TOTAL ROOM LATENT |  |  | 783.8687 | 1132.1998
III | TOTAL ROOM HEAT LOAD |  |  | 6728.7676 | 5699.8133
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.9355 | 13.9987
| PRELIMINARY S.A.V. (m3/s) |  |  | 0.48023 | 0.3713
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 590.6776 | 456.7027
V | FAN GAIN (W) |  |  | 250 | 200
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 0.54814 | 0.42469
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0084727 | 0.0086213
| MIXING RATIO (% FRESH AIR) |  |  | 0 | 0
| COIL BYPASS FACTOR |  |  | 0.2 | 0.2
| TEMPERATURE OF MIXED AIR (OC) |  |  | 24 | 24
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.0089478 | 0.009507
| WADP OF COOLING COIL |  |  | 0.0083539 | 0.0083999
| TADP OF COOLING COIL (OC) |  |  | 11.4193 | 11.4984
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.9355 | 13.9987
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 6785.5765 | 5224.3162
VII | COOLING COIL LATENT LOAD (W) |  |  | 783.8687 | 1132.1998 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 7569.4452 | 6356.516
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 2.1522 | 1.8074 | I | COIL LOAD |  | 2.3675 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 2170.6151 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 1973.2865 | 1528.8718 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 300 | 300 |  | CFM/Tr |  | 539
| BLOWER MOTOR I/P (kW) |  |  | 0.25 | 0.2 |  | Sq.m/Tr |  | 8.8

## MS room
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Pediatric Unit | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 25 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 46
HUMIDITY RATIO |  |  | 0.016835 | 0.009121
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 25
RELATIVE HUMIDITY |  |  | 72 | 53
HUMIDITY RATIO |  |  | 0.022181 | 0.010509
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  | 19.61 | 2.28 | 12.45 | 556.6495 | 2.95 | 131.8969
2 | EXT. WALL NE |  |  |  |  | 2.28 | 12.85 | 0 | 4.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 12.85 | 0 | 7.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 10.15 | 0 | 9.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 8.95 | 0 | 10.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 10.95 | 0 | 10.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 14.05 | 0 | 9.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 13.65 | 0 | 4.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  | 5.883 | 5.23 | 9.85 | 303.0657 | 4.95 | 152.302 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 81.06 | 2.28 | 9.2 | 1700.3146 | 4.3 | 794.7122
18 | INT. GLASS. |  |  |  |  | 7.1 | 9.2 | 0 | 4.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 9.2 | 0 | 4.3 | 0
20 | ROOF EXPOSED |  |  |  | 37.1 | 0.7 | 28.65 | 744.0405 | 22.75 | 590.8175
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 37.1 | 3.19 | 9.2 | 1088.8108 | 4.3 | 508.9007
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 9.85 | 0 | 4.95 | 0 |  | 6.7 | 6.7 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 4392.881 |  | 2178.6293
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 18 | 18 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 5.883 | 0.7 | 0.91 | 237 | 888.1506 | 0.91 | 101 | 378.4946 |  | 0.91 | 0.91 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.12 | 625 | 0 | 0.12 | 199 | 0 |  | 0.12 | 0.12 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.12 | 644 | 0 | 0.12 | 675 | 0 |  | 0.12 | 0.12 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.13 | 284 | 0 | 0.13 | 767 | 0 |  | 0.13 | 0.13 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.19 | 126 | 0 | 0.19 | 565 | 0 |  | 0.19 | 0.19 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.45 | 284 | 0 | 0.45 | 767 | 0 |  | 0.45 | 0.45 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.61 | 644 | 0 | 0.61 | 675 | 0 |  | 0.61 | 0.61 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.69 | 625 | 0 | 0.69 | 199 | 0 |  | 0.69 | 0.69 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.25 | 864 | 0 | 0.25 | 820 | 0 |  | 0.25 | 0.25 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 888.1506 |  | 712.4725 | 644.1532 | 634.3933 | 712.4725 | 780.7918 | 839.3511 | 868.6308 | 868.6308 | 839.3511 | 800.3116 | 731.9923 | 761.272 | 888.1506
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 888.1506 |  |  | 378.4946 |  |  | 378.4946 | 303.6275 | 274.5125 | 270.3533 | 303.6275 | 332.7425 | 357.6982 | 370.176 | 370.176 | 357.6982 | 341.061 | 311.9461 | 324.4239 | 378.4946
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 3 | x | 60 | 1 | 180
2 | NO. | 3 | x | 70 |  |  | 210
C | TOTAL BODY GAIN. |  |  |  |  | 180 | 210
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 3 | x | 37.1 | 1 | 1 | 111.3
6 | AREA LOADING POWER | 10 | x | 37.1 | 1 | 1 | 371
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 482.3 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 37.1 | 4.2 | 1 | + |  | 155.82 | 649.5097 | 1004.9669 | 388.6411 | 1520.6967
E | TOTAL INFILTRATION GAINS. | [5 empty] | 649.5097 | 1004.9669 | 388.6411 | 1520.6967
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 4392.881 | 2178.6293 |  | Room S.H.R. (%) |  | 84.44% | 67.58%
2 | SOLAR. |  |  | 888.1506 | 378.4946 |  | No. of Air Changes per hour |  | 13 | 7
3 | BODY |  |  | 180 | 180 |  | TOUT, BAL (OC) |  | -27.0561 | -0.20603
4 | EQUIPMENT |  |  | 482.3 | 482.3 |  | Solar time used for glass load |  | 18 | 18
5 | INFILTRATION. |  |  | 649.5097 | 388.6411
I | TOTAL ROOM SENSIBLE |  |  | 6592.8413 | 3608.065
1 | BODY |  |  | 210 | 210
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 1004.9669 | 1520.6967
II | TOTAL ROOM LATENT |  |  | 1214.9669 | 1730.6967
III | TOTAL ROOM HEAT LOAD |  |  | 7807.8082 | 5338.7617
| ROOM SUPPLY AIR TEMP (OC) |  |  | 13.9068 | 13.6901
| PRELIMINARY S.A.V. (m3/s) |  |  | 0.48318 | 0.25936
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 594.3156 | 319.0185
V | FAN GAIN (W) |  |  | 250 | 140
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 0.54506 | 0.29236
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0083805 | 0.0085423
| MIXING RATIO (% FRESH AIR) |  |  | 0 | 0
| COIL BYPASS FACTOR |  |  | 0.2 | 0.2
| TEMPERATURE OF MIXED AIR (OC) |  |  | 25 | 25
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.009121 | 0.010509
| WADP OF COOLING COIL |  |  | 0.0081953 | 0.0080507
| TADP OF COOLING COIL (OC) |  |  | 11.1335 | 10.8626
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 13.9068 | 13.6901
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 7437.1569 | 4067.0834
VII | COOLING COIL LATENT LOAD (W) |  |  | 1214.9669 | 1730.6967 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 8652.1238 | 5797.7801
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 2.4601 | 1.6485 | I | COIL LOAD |  | 2.7061 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 2158.4477 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 1962.2252 | 1052.4996 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 300 | 300 |  | CFM/Tr |  | 469
| BLOWER MOTOR I/P (kW) |  |  | 0.25 | 0.14 |  | Sq.m/Tr |  | 13.7

## X-Ray
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | ESIC Hospital, Thirippur, Pediatric Unit | [5 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 25 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 44
HUMIDITY RATIO |  |  | 0.016835 | 0.0087245
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 25
RELATIVE HUMIDITY |  |  | 72 | 45
HUMIDITY RATIO |  |  | 0.022181 | 0.0089227
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 12.45 | 0 | 2.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 12.85 | 0 | 4.05 | 0
3 | EXT. WALL E |  |  |  | 26.25 | 2.28 | 12.85 | 769.0725 | 7.95 | 475.8075
4 | EXT. WALL SE |  |  |  |  | 2.28 | 10.15 | 0 | 9.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 8.95 | 0 | 10.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 10.95 | 0 | 10.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 14.05 | 0 | 9.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 13.65 | 0 | 4.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  | 7.875 | 5.23 | 3.15 | 129.7367 | -1.75 | -72.0759 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  | 73.92 | 2.28 | 9.2 | 1550.5459 | 4.3 | 724.7117
18 | INT. GLASS. |  |  |  |  | 7.1 | 9.2 | 0 | 4.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 9.2 | 0 | 4.3 | 0
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 28.65 | 0 | 22.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  | 25.9 | 3.19 | 9.2 | 760.1132 | 4.3 | 355.2703
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 3.15 | 0 | -1.75 | 0 |  | 0 | 0 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 3209.4683 |  | 1483.7135
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 8 | 8 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.65 | 237 | 0 | 0.65 | 101 | 0 |  | 0.65 | 0.65 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.74 | 625 | 0 | 0.74 | 199 | 0 |  | 0.74 | 0.74 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 7.875 | 0.7 | 0.8 | 644 | 2840.04 | 0.8 | 675 | 2976.75 |  | 0.8 | 0.8 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.74 | 284 | 0 | 0.74 | 767 | 0 |  | 0.74 | 0.74 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.23 | 126 | 0 | 0.23 | 565 | 0 |  | 0.23 | 0.23 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.14 | 284 | 0 | 0.14 | 767 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.11 | 644 | 0 | 0.11 | 675 | 0 |  | 0.11 | 0.11 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.14 | 625 | 0 | 0.14 | 199 | 0 |  | 0.14 | 0.14 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.44 | 864 | 0 | 0.44 | 820 | 0 |  | 0.44 | 0.44 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 2840.04 |  | 1668.5235 | 2556.036 | 2840.04 | 2698.038 | 2201.031 | 1455.5205 | 958.5135 | 923.013 | 852.012 | 781.011 | 710.01 | 568.008 | 426.006
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 2840.04 |  |  | 2976.75 |  |  | 2976.75 | 1748.8406 | 2679.075 | 2976.75 | 2827.9125 | 2306.9812 | 1525.5844 | 1004.6531 | 967.4438 | 893.025 | 818.6063 | 744.1875 | 595.35 | 446.5125
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. | 2 | x | 60 | 1 | 120
2 | NO. | 2 | x | 70 |  |  | 140
C | TOTAL BODY GAIN. |  |  |  |  | 120 | 140
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES | 1 | x | 40000 | 0.1 | 1 | 4000
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT | 5 | x | 25.9 | 1 | 1 | 129.5
6 | AREA LOADING POWER | 30 | x | 25.9 | 1 | 1 | 777
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 4906.5 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 | 25.9 | 4.2 | 1 | + |  | 108.78 | 453.4313 | 737.6492 | 271.3154 | 1205.8927
E | TOTAL INFILTRATION GAINS. | [5 empty] | 453.4313 | 737.6492 | 271.3154 | 1205.8927
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 3209.4683 | 1483.7135 |  | Room S.H.R. (%) |  | 92.93% | 87.88%
2 | SOLAR. |  |  | 2840.04 | 2976.75 |  | No. of Air Changes per hour |  | 32 | 27
3 | BODY |  |  | 120 | 120 |  | TOUT, BAL (OC) |  | -34.8746 | -19.1472
4 | EQUIPMENT |  |  | 4906.5 | 4906.5 |  | Solar time used for glass load |  | 8 | 8
5 | INFILTRATION. |  |  | 453.4313 | 271.3154
I | TOTAL ROOM SENSIBLE |  |  | 11529.4396 | 9758.279
1 | BODY |  |  | 140 | 140
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 737.6492 | 1205.8927
II | TOTAL ROOM LATENT |  |  | 877.6492 | 1345.8927
III | TOTAL ROOM HEAT LOAD |  |  | 12407.0888 | 11104.1717
| ROOM SUPPLY AIR TEMP (OC) |  |  | 14.1319 | 13.9631
| PRELIMINARY S.A.V. (m3/s) |  |  | 0.86248 | 0.71882
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 1060.8527 | 884.1539
V | FAN GAIN (W) |  |  | 450 | 370
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 0.9755 | 0.81121
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.0084256 | 0.0083715
| MIXING RATIO (% FRESH AIR) |  |  | 0 | 0
| COIL BYPASS FACTOR |  |  | 0.2 | 0.2
| TEMPERATURE OF MIXED AIR (OC) |  |  | 25 | 25
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.0087245 | 0.0089227
| WADP OF COOLING COIL |  |  | 0.0083508 | 0.0082337
| TADP OF COOLING COIL (OC) |  |  | 11.4149 | 11.2039
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 14.1319 | 13.9631
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 13040.2923 | 11012.4329
VII | COOLING COIL LATENT LOAD (W) |  |  | 877.6492 | 1345.8918 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 13917.9414 | 12358.3247
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 3.9573 | 3.5139 | I | COIL LOAD |  | 4.3531 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 3862.9961 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 3511.8146 | 2920.3526 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 300 | 300 |  | CFM/Tr |  | 522
| BLOWER MOTOR I/P (kW) |  |  | 0.45 | 0.37 |  | Sq.m/Tr |  | 5.9