## OUTLETS & FLOW
LIST OF GAS OUTLETS FOR 100 BEDDED HOSPITAL
|  |  | GAS OUTLETS | [11 empty] | ACCESSORIES |  |  |  | ZONAL VALVE BOXES |  | AREA ALARM PANEL
S.NO. | FLOOR & LOCATION | BEDS | OXYGEN | Unit Diversified flow | Mains Diversified flow | N2O | MA4 | Unit Diversified flow | Mains Diversified flow | VACUUM | Unit Diversified flow | Mains Diversified flow | N2 | AGSS | FLOW METER | WARD VACUUM UNIT | BED HEAD PANEL | THEATER SUCTION TROLLEY | 2 GAS SERVICES | 3 GAS SERVICES | 2 GAS SERVICES | 3 GAS SERVICES | ZONE
|  |  |  | (lpm) | (lpm) |  |  | (lpm) | (lpm) |  | (lpm) | (lpm)
| GROUND FLOOR | [18 empty] | 1
1 | X- Ray |  | 1 | 10 | 10 |  |  |  |  | 1 | 40 | 40 |  |  | 1 | 1 |  |  | 1 |  | 1 |  | 1
2 | X-Ray |  | 1 | 10 | 10 |  |  |  |  | 1 | 40 | 40 |  |  | 1 | 1 | [6 empty] | 1
3 | Emergency OT
3.1 | Anesthesia/ Surgeon Pendant |  | 2 | 100 | 100 | 2 | 2 | 40 | 40 | 2 | 80 | 80 | 1 | 2 |  |  |  | 1 |  | 2 |  | 2 | 2
4 | Post Procedural Room | 2 | 2 | 16 | 16 |  | 2 | 50 | 50 | 2 | 50 | 50 |  |  | 2 | 2 | 2 |  |  | 1 |  | 1 | 3
5 | Isolation Ward | 2 | 2 | 10.6 | 10.6 |  | 2 | 22.5 | 22.5 | 2 | 40 | 40 |  |  | 2 | 2 | 2 | [5 empty] | 3
6 | Resuscitation | 2 | 2 | 101.5 | 101.5 |  | 2 | 45 | 45 | 2 | 50 | 50 |  |  | 2 | 2 | 2 | [5 empty] | 3
7 | Treatmet room |  | 1 | 10 | 10 |  |  | 40 | 40 | 1 | 30 | 30 |  |  | 1 | 1 | [6 empty] | 3
8 | Emergency Ward | 6 | 6 | 13 | 13 |  | 6 | 32.5 | 32.5 | 6 | 40 | 40 |  |  | 6 | 6 | 6 |  |  | 1 |  | 1 | 4
9 | CSSD | [11 empty] | 1 | [5 empty] | 1
| FIRST FLOOR | [18 empty] | 1
1 | ICU | 10 | 20 | 50.5 | 50.5 |  | 20 | 440 | 440 | 20 | 130 | 130 |  |  | 10 | 10 | 10 |  |  | 1 |  | 1 | 5
2 | PICU |  | 6 | 22 | 22 |  | 6 | 120 | 120 | 6 | 60 | 60 |  |  | 3 | 3 |  |  |  | 1 |  | 1 | 6
3 | HDU |  | 6 | 22 | 22 |  | 6 | 120 | 120 | 6 | 60 | 60 |  |  | 3 | 3 |  |  |  | 1 |  | 1 | 7
4 | Nursery |  | 2 | 11.5 | 11.5 |  |  | 40 | 40 | 2 | 40 |  |  |  | 2 | 2 | [6 empty] | 7
5 | NICU |  | 8 | 28 | 28 |  | 8 | 160 | 160 | 8 | 70 | 70 |  |  | 4 | 4 |  |  |  | 1 |  | 1 | 8
4 | Isolation Room |  | 1 | 10 | 5 |  | 1 | 20 | 20 | 1 | 40 | 10 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 9
5 | Treatment Room |  | 1 | 10 | 10 |  |  | 40 |  | 1 | 40 | 40 |  |  | 1 | 1 | [5 empty] | 1 | 9
6 | Casualty with Observation ward | 2 | 4 | 14.5 | 14.5 |  | 4 | 45 | 45 | 4 | 50 | 50 |  |  | 2 | 2 | 2 | [5 empty] | 9
7 | Examination Room |  | 1 | 10 | 10 |  |  |  |  | 1 | 40 | 40 |  |  | 1 | 1 | [6 empty] | 9
8 | Minor Procedure Room |  | 1 | 10 | 10 |  |  |  |  | 1 | 40 | 40 |  |  | 1 | 1 | [6 empty] | 9
9 | Pre Labour | 3 | 3 | 13 | 13 |  |  |  |  | 3 | 40 | 40 |  |  | 3 | 3 | 3 |  |  | 1 |  | 1 | 10
10 | Labour Room | 2 | 4 | 11.5 | 11.5 |  | 2 | 50 | 50 | 4 | 50 | 50 |  |  | 2 | 2 | 2 | [5 empty] | 10
10.1 | Baby Resus |  | 2 | 11.5 | 11.5 |  | 2 | 40 | 40 | 2 | 40 |  |  |  | 2 | 2 | [6 empty] | 10
11 | Post Labour | 4 | 4 | 14.5 | 14.5 |  |  |  |  | 4 | 70 | 70 |  |  | 4 | 4 | 4 | [5 empty] | 10
12 | Isolation Ward | 2 | 2 | 11.5 | 5.75 |  | 2 | 22.5 | 11.25 | 2 | 40 | 10 |  |  | 2 | 2 | 2 | [5 empty] | 10
13 | Treatment Room |  | 1 | 10 | 10 |  |  |  |  | 1 | 40 | 40 |  |  | 1 | 1 |  |  | 1 |  | 1 |  | 11
14 | Ward | 6 | 6 | 17.5 | 17.5 |  |  |  |  | 6 | 40 | 40 |  |  | 6 | 6 | [6 empty] | 11
15 | Ward | 6 | 6 | 17.5 | 8.75 |  |  |  |  | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 11
16 | Ward | 6 | 6 | 17.5 | 8.75 |  |  |  |  | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 11
17 | Post Holding | 6 | 6 | 40 | 40 |  | 6 | 52.5 | 52.5 | 6 | 90 | 90 |  |  | 6 | 6 | 6 |  |  | 1 |  | 1 | 12
18 | Pre-Op holding | 5 | 5 | 28 | 28 |  | 5 | 40 |  | 5 | 40 | 40 |  |  | 5 | 5 | 5 |  |  | 1 |  | 1 | 13
19 | Isolation Ward | 2 | 2 | 11.5 | 5.75 |  | 2 | 22.5 | 11.25 | 2 | 40 | 40 |  |  | 2 | 2 | 2 | [5 empty] | 13
20 | Operation Theater-1 |  |  | 100 | 100 |  |  | 40 | 40 | [10 empty] | 2 |  | 2 | 14
| Anesthesia Pendant |  | 2 |  |  | 2 | 2 |  |  | 2 | 40 | 40 |  | 2 |  |  |  | 1 |  |  |  |  | 14
| Surgeon Pendant |  | 2 | [6 empty] | 2 | 40 | 40 | 1 | [9 empty] | 14
21 | Operation Theater-2 |  |  | 100 | 10 |  |  | 40 | 10 | [10 empty] | 2 |  | 2 | 15
| Anesthesia Pendant |  | 2 |  |  | 2 | 2 |  |  | 2 | 40 | 40 |  | 2 |  |  |  | 1 |  |  |  |  | 15
| Surgeon Pendant |  | 2 | [6 empty] | 2 | 40 | 40 | 1 | [9 empty] | 15
22 | Operation Theater-3 |  |  | 100 | 10 |  |  | 40 | 10 | [10 empty] | 2 |  | 2 | 16
| Anesthesia Pendant |  | 2 |  |  | 2 | 2 |  |  | 2 | 40 | 40 |  | 2 |  |  |  | 1 |  |  |  |  | 16
| Surgeon Pendant |  | 2 | [6 empty] | 2 | 40 | 40 | 1 | [9 empty] | 16
| SECOND FLOOR | [18 empty] | 1
1 | Ward | 8 | 8 | 20.5 | 20.5 |  |  | 37.5 | 37.5 | 8 | 40 | 40 |  |  | 8 | 8 |  |  | 1 |  | 1 |  | 17
2 | Ward | 8 | 8 | 20.5 | 10.25 |  |  | 37.5 | 18.75 | 8 | 40 | 10 |  |  | 8 | 8 | [6 empty] | 17
3 | Ward | 8 | 8 | 20.5 | 10.25 |  |  | 37.5 | 18.75 | 8 | 40 | 10 |  |  | 8 | 8 | [6 empty] | 17
4 | Ward | 7 | 7 | 19 | 9.5 |  |  | 35 | 17.5 | 7 | 40 | 10 |  |  | 7 | 7 | [6 empty] | 17
5 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 |  |  | 1 |  | 1 |  | 18
6 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 18
7 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 18
8 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 18
9 | Ward | 2 | 2 | 11.5 | 5.75 |  |  | 22.5 | 11.25 | 2 | 40 | 10 |  |  | 2 | 2 | [6 empty] | 18
10 | Examination Treatment Room |  | 1 | 10 | 10 |  |  | 40 |  | 1 | 40 | 40 |  |  | 1 | 1 | [6 empty] | 18
11 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 |  |  | 1 |  | 1 |  | 19
12 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 19
13 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 19
14 | Ward | 6 | 6 | 17.5 | 8.75 |  |  | 32.5 | 16.25 | 6 | 40 | 10 |  |  | 6 | 6 | [6 empty] | 19
15 | Ward | 2 | 2 | 11.5 | 5.75 |  |  | 22.5 | 11.25 | 2 | 40 | 10 |  |  | 2 | 2 | [6 empty] | 19
| Plant room OT |  |  | 100 |  | 1 |  | 40 |  |  | 40 |  | 1 | 1
| Plant room external |  | 1 | 100 |  |  | 1 | 40 |  | 1 | 40
| Overall diversity |  | 0.8 |  |  |  | 0.8 |  |  | 0.7
| Future expantion |  | 1.3 |  |  |  | 1.3 |  |  | 1.3
| TOTAL # | 149 | 211 |  |  | 9 | 85 |  |  | 211 |  |  | 6 | 9 | 172 | 172 | 48 | 4 | 6 | 20 | 5 | 19
| TOTAL FLOW (LPM) |  | 930 |  |  | 33 | 1720 |  |  | 1610 |  |  | 612.5 | 520

## GAS LINE SIZING
GAS LINE SIZING
|  |  | OXYGEN |  |  | MA4 |  |  | VACCUM
S.NO. | ZONE | LENGTH | # | FLOW | LINE SIZE | # | FLOW | LINE SIZE | # | FLOW | LINE SIZE
|  | (m) |  | (lpm) | (mm) |  | (lpm) | (mm) |  | (lpm) | (mm)
GROUND FLOOR
1 | Zone 1 | 20 | 2 | 20 | 12 | 0 | 0 |  | 2 | 80 | 22
2 | Zone 2 | 20 | 2 | 100 | 12 | 2 | 40 | 12 | 2 | 80 | 22
3 | Zone 3 | 40 | 7 | 138.1 | 15 | 6 | 157.5 | 15 | 7 | 170 | 22
4 | Zone 4 | 35 | 6 | 13 | 12 | 6 | 32.5 | 12 | 6 | 40 | 22
| Overall diversity & future expansion |  |  | 1.17 |  |  | 1.17 |  |  | 1.04
| Ground Floor Sub Main | 80 | 17 | 317.187 | 22 | 14 | 230 | 22 | 17 | 370 | 28
FIRST FLOOR
5 | Zone 5 | 55 | 20 | 50.5 | 12 | 20 | 440 | 22 | 20 | 130 | 22
6 | Zone 6 | 20 | 6 | 22 | 12 | 6 | 120 | 15 | 6 | 60 | 22
7 | Zone 7 | 35 | 8 | 33.5 | 12 | 6 | 160 | 15 | 8 | 60 | 22
8 | Zone 8 | 25 | 8 | 28 | 12 | 8 | 160 | 15 | 8 | 70 | 22
9 | Zone 9 | 40 | 8 | 49.5 | 12 | 5 | 65 | 12 | 8 | 180 | 22
10 | Zone 10 | 70 | 15 | 56.25 | 12 | 6 | 101.25 | 15 | 15 | 170 | 22
11 | Zone 11 | 80 | 19 | 45 | 12 | 0 | 0 |  | 19 | 100 | 22
12 | Zone 12 | 30 | 6 | 40 | 12 | 6 | 52.5 | 12 | 6 | 90 | 22
13 | Zone 13 | 50 | 7 | 33.75 | 12 | 7 | 11.25 | 12 | 7 | 80 | 22
14 | Zone 14 | 20 | 4 | 100 | 12 | 2 | 40 | 12 | 4 | 80 | 22
15 | Zone 15 | 20 | 4 | 10 | 12 | 2 | 10 | 12 | 4 | 80 | 22
16 | Zone 16 | 20 | 4 | 10 | 12 | 2 | 10 | 12 | 4 | 80 | 22
| Overall diversity & future expansion |  |  | 1.17 |  |  | 1.17 |  |  | 1.04
| First Floor Sub Main | 250 | 109 | 559.845 | 28 | 70 | 1368.9 | 35 | 109 | 1227.2 | 54
SECOND FLOOR
17 | Zone 17 | 110 | 31 | 50.5 | 12 | 0 | 92.5 | 12 | 31 | 70 | 22
18 | Zone 18 | 100 | 27 | 50.75 | 12 | 0 | 76.25 | 12 | 27 | 90 | 22
19 | Zone 19 | 110 | 26 | 40.75 | 12 | 0 | 76.25 | 12 | 26 | 50 | 22
| Overall diversity & future expansion |  |  | 1.17 |  |  | 1.17 |  |  | 1.04
| Second Floor Sub Main | 90 | 84 | 166.14 | 22 | 0 | 286.65 | 22 | 84 | 218.4 | 28
| Mains from plant room | 190 | 211 | 930 | 35 | 85 | 1720 | 42 | 211 | 1610 | 76
| No of J size cylinders required per gas bank for 2 day backup @ 10% average usage |  |  | 41 | Nos
| No of J size cylinders required per gas bank for 4 hrs backup @ 25% average usage |  |  | 9 | Nos
| LOX plant required for 8 day backup @ 10% average usage |  |  | 1100 | s.cum
Notes:
Design pressure drop taken as follows
| Service | Zones | S.Main | Main
|  | (bar) | (bar) | (bar)
| Oxygen | 0.07 | 0.07 | 0.07
| MA4 | 0.07 | 0.07 | 0.09
| Vaccum | 0.07 | 0.04 | 0.04
Abstract of Measurements
| Service | 12 | 15 | 22 | 28 | 35 | 42 | 54 | 76
| Oxygen | 860 | 40 | 170 | 250 | 190 | 0 | 0 | 0
| MA4 | 555 | 190 | 225 | 0 | 250 | 190 | 0 | 0
| Vaccum | 0 | 0 | 900 | 170 | 0 | 0 | 250 | 190
| N2O | 90
| N2 |  | 40 | 50
| AGSS |  |  | 40 | 50
| Outlet drops | 888 | 633
| Total | 2390 | 900 | 1390 | 470 | 440 | 190 | 250 | 190
Plant capacity proposed
| Oxygen | 1100 s.cum LOX plant for primary supply with 10+10 cylinder manifold system as secondary supply.
| MA4 | 3 x 30 CFM compressor station
| Vaccum | 3 x 30 CFM vaccum compressor station
| N2O | 3+3 cylinder manifold system
| N2 | 3+3 cylinder manifold system
| AGSS | 520 LPM duplex LGSS system