## Lighting calculation sheet
INTERNAL LIGHTING CALCULATION SHEET (ZONAL CAVITY METHOD)
|  |  | Reflectance factors | [13 empty] | Required |  |  | Selected | [5 empty] | Room index vs Uf
S.N | Room | Polar Pattern | Floor | Ceiling | Wall | L | B | H | Working level (h) | Fixture level (Hf) | Required lux | Room index (K) | Uf | Mf | Lamp power | Lamp Flux | # | Nl | Nb | Nl | Nb | # | Actual lux | Energy density | SHR | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[6 empty] | (m) | (m) | (m) | (m) | (m) | (lx) |  |  |  | (W) | (lm) | [6 empty] | (lx) | (W/sqm) | (<1.5)
Ground Floor
1 | Room 1 | Batten | 20 | 70 | 50 | 5 | 4 | 4.2 | 0.85 | 0.5 | 300 | 0.77973 | 0.96 | 0.722 | 20 | 2000 | 4.3283 | 2.326 | 1.8608 | 2 | 2 | 4 | 280 | 4 | 0.78459 | 114 | 96 | 83 | 72 | 64 | 57 | 51 | 46 | 42 | 39 | 36
2 | Room 2 | 2x2 panel | 20 | 70 | 50 | 5 | 4 | 4.2 | 0.85 | 1 | 500 | 0.94563 | 1.04 | 0.722 | 36 | 3600 | 3.6994 | 2.1504 | 1.7203 | 2 | 2 | 4 | 540 | 7.2 | 0.95152 | 116 | 104 | 92 | 82 | 74 | 67 | 60 | 55 | 51 | 47 | 43
3 | Room 3 | R.Down | 20 | 70 | 50 | 15 | 2.5 | 4.2 | 0.85 | 1 | 100 | 0.91185 | 0.96 | 0.722 | 15 | 1500 | 3.6069 | 4.652 | 0.77534 | 5 | 1 | 5 | 140 | 2 | 1.1654 | 107 | 96 | 86 | 77 | 69 | 63 | 57 | 52 | 48 | 45 | 41
4 | Room 4 | S.Down | 20 | 70 | 50 | 15 | 2.5 | 4.2 | 0.85 | 0 | 200 | 0.63966 | 1.01 | 0.722 | 15 | 1500 | 6.8566 | 6.414 | 1.069 | 7 | 1 | 7 | 200 | 2.8 | 0.69091 | 116 | 101 | 88 | 77 | 68 | 61 | 55 | 50 | 46 | 42 | 39