## submersible pump
HEAD CALCULATION SHEET FOR CHILLED WATER PUMP
Sl.No | Type | Desc | Nos | Length | dia | Discharge | v | Re | e | f | K | Head loss | Cumulative
|  |  |  | m | mm | l/s | m/s
1 | Pipe | Suction line motor |  | 3 | 125 | 16.85 | 1.37 | 214062.5 | 0.2 | 0.0224 |  | 0.051 | 0.051
2 | Fitting | Bend | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.7 | 0.067 | 0.118
3 | Fitting | Butterfly suction | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.4 | 0.038 | 0.156
4 | Fitting | Y strainer suction | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 10 | 0.958 | 1.114
5 | Fitting | NRV delivery | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 2.3 | 0.22 | 1.334
6 | Fitting | Butterfly delivery | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.4 | 0.038 | 1.372
7 | Pipe | Delivery line |  | 3 | 125 | 16.85 | 1.37 | 214062.5 | 0.2 | 0.0224 |  | 0.051 | 1.423
8 | Fitting | Tee Delivery | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 1.8 | 0.172 | 1.595
9 | Pipe | Delivery header |  | 3 | 150 | 33.7 | 1.91 | 358125 | 0.2 | 0.0213 |  | 0.079 | 1.674
10 | Fitting | Bends | 2 |  | 150 | 33.7 | 1.91 |  |  |  | 0.7 | 0.261 | 1.935
11 | Fitting | Tee | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 1.8 | 0.172 | 2.107
12 | Pipe | Chiller suction |  | 3 | 125 | 16.85 | 1.37 | 214062.5 | 0.2 | 0.0224 |  | 0.051 | 2.158
13 | Fitting | Bends | 2 |  | 125 | 16.85 | 1.37 |  |  |  | 0.7 | 0.134 | 2.292
14 | Fitting | Butterfly suction | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.4 | 0.038 | 2.33
15 | Equipment | Chiller coil |  |  | 125 | 5.055 | 0.41 |  |  |  |  | 7 | 9.33
16 | Fitting | Balancing valve | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.2 | 0.019 | 9.349
17 | Fitting | Butterfly delivery | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 0.4 | 0.038 | 9.387
18 | Pipe | Chiller delivery |  | 3 | 125 | 16.85 | 1.37 | 214062.5 | 0.2 | 0.0224 |  | 0.051 | 9.438
19 | Fitting | Tee | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 1.8 | 0.172 | 9.61
20 | Pipe | Chiller out line |  | 20 | 150 | 33.7 | 1.91 | 358125 | 0.2 | 0.0213 |  | 0.529 | 10.139
21 | Fitting | Bends | 3 |  | 150 | 33.7 | 1.91 |  |  |  | 0.7 | 0.391 | 10.53
22 | Fitting | Butterfly | 1 |  | 150 | 33.7 | 1.91 |  |  |  | 0.4 | 0.074 | 10.604
23 | Fitting | Tee | 1 |  | 125 | 25.275 | 2.06 |  |  |  | 1.8 | 0.39 | 10.994
24 | Pipe | BSL3 in line |  | 10 | 125 | 25.275 | 2.06 | 321875 | 0.2 | 0.0221 |  | 0.383 | 11.377
25 | Fitting | Bends | 2 |  | 125 | 25.275 | 2.06 |  |  |  | 0.7 | 0.303 | 11.68
26 | Fitting | Tee | 1 |  | 80 | 5.055 | 1.01 |  |  |  | 1.8 | 0.094 | 11.774
27 | Pipe | AHU line in |  | 3 | 80 | 5.055 | 1.01 | 101000 | 0.2 | 0.025 |  | 0.049 | 11.823
28 | Fitting | Bends | 4 |  | 80 | 5.055 | 1.01 |  |  |  | 0.7 | 0.146 | 11.969
29 | Fitting | Three way valve | 1 |  | 80 | 5.055 | 1.01 |  |  |  | 0.8 | 0.042 | 12.011
30 | Equipment | Cooling coil 8 row |  |  | 80 | 5.055 | 1.01 |  |  |  |  | 8 | 20.011
31 | Pipe | AHU line out |  | 3 | 80 | 5.055 | 1.01 | 101000 | 0.2 | 0.025 |  | 0.049 | 20.06
32 | Fitting | Tee | 1 |  | 80 | 5.055 | 1.01 |  |  |  | 1.8 | 0.094 | 20.154
33 | Pipe | BSL3 out line |  | 10 | 125 | 25.275 | 2.06 | 321875 | 0.2 | 0.0221 |  | 0.383 | 20.537
34 | Fitting | Bends | 3 |  | 125 | 25.275 | 2.06 |  |  |  | 0.7 | 0.455 | 20.992
35 | Fitting | Tee | 1 |  | 125 | 25.275 | 2.06 |  |  |  | 1.8 | 0.39 | 21.382
36 | Pipe | Chiller in line |  | 20 | 150 | 33.7 | 1.91 | 358125 | 0.2 | 0.0213 |  | 0.529 | 21.911
37 | Fitting | Bends | 2 |  | 150 | 33.7 | 1.91 |  |  |  | 0.7 | 0.261 | 22.172
38 | Fitting | Butterfly | 1 |  | 150 | 33.7 | 1.91 |  |  |  | 0.4 | 0.074 | 22.246
39 | Fitting | Tee suction motor | 1 |  | 125 | 16.85 | 1.37 |  |  |  | 1.8 | 0.172 | 22.418
40 | Gravity | Head diff b/w motor and final outlet max |  | 0 | [7 empty] | 0 | 22.418
|  | Say after 10% safety factor |  | (m) | [8 empty] | 25
|  | Power of motor with 60% pump efficiency, 90% motor efficiency and 20% safety margin |  | (hp) | [8 empty] | 12.3

## e values
PVC | 0.0015
Concrete | 0.3 | 3
GI | 0.15

## kl value
k
Globe valve (fully open) | 6.4
Globe valve (half open) | 9.5
Angle valve (fully open) | 5
Swing check valve (fully open) | 2.5
Butterfly valve (fully open) | 0.4
Gate valve (fully open) | 0.2
Gate valve (3/4 open) | 1
Gate valve (half open) | 5.6
Gate valve (one-quarter open) | 24
Check valve, swing type (fully open) | 2.3
Check valve, lift type (fully open) | 12
Check valve, ball type (fully open) | 70
Foot Valve (fully open) | 15
Close return bend (180º) | 2.2
Standard tee | 1.8
Standard (short radius) elbow (90º) | 0.9
Medium radius elbow (90º) | 0.7
Long sweep elbow (90º) | 0.6
45 degree elbow | 0.4
Pipe entrance (Square-edged) | 0.5
Pipe entrance (Re-entrant) | 0.8
Pipe entrance (Rounded, r/D < 0.16) | 0.1
Pipe exit | 1
Sudden contraction (2 to 1) | 0.25
Sudden contraction (5 to 1) | 0.41
Sudden contraction (10 to 1) | 0.46
Orifice plate (1.5 to 1) | 0.85
Orifice plate (2 to 1) | 3.4
Orifice plate (4 to 1) | 29
Sudden enlargement | (1-A1/A2)2
90 degree miter bend (without vanes) | 1.1
90 degree miter bend (with vanes) | 0.2
General contraction (30 degree included angle) | 0.02
General contraction (70 degree included angle) | 0.07
Tee, Flanged, Dividing Line Flow | 0.2
Tee, Threaded, Dividing Line Flow | 0.9
Tee, Flanged, Dividing Branched Flow | 1
Tee, Threaded , Dividing Branch Flow | 2
Y stariner | 2 (clean) to 10 (dirty)