## ROOM 1
HEAT LOAD ESTIMATION SHEET
JOB/REF No. | [6 empty] | ESTIMATED BY:- |  | DATE:-
LOCATION:- | [6 empty] | CHECKED BY:- |  | DATE:-
SHEET | 1 | OF | 1 |  |  |  | APPROVED BY:- |  | DATE:-
DESIGN DATA
SUMMER |  |  | To, OC | Ti, OC | DR OC |  | Notes:
d.b. TEMPERATURE |  |  | 37.2 | 26 |  |  | 1. All dimensions in metres.
RELATIVE HUMIDITY |  |  | 41 | 50
HUMIDITY RATIO |  |  | 0.016835 | 0.010542
DAILY RANGE |  |  |  |  | 10.5
RAINY
d.b. TEMPERATURE |  |  | 32.3 | 26
RELATIVE HUMIDITY |  |  | 72 | 50
HUMIDITY RATIO |  |  | 0.022181 | 0.010542
DAILY RANGE |  |  |  |  | 10.5
LATITUDE:- |  |  | 12°N
| WALL:- | LIGHT | MEDIUM | DARK
| ROOF:- | LIGHT | MEDIUM | DARK
| GLAZING:- | BLINDS | SHADE | BARE
TRANSMITTED HEAT GAINS AND LOSSES
ITEM | DESCRIPTION |  |  |  | AREA, | U | SUMMER | HEAT | RAINY | HEAT
No. |  |  |  |  | m2 | VALUE | TEMP DIFF OC | GAIN, W. | TEMP DIFF OC | GAIN, W.
1 | EXT. WALL N |  |  |  |  | 2.28 | 11.45 | 0 | 1.95 | 0
2 | EXT. WALL NE |  |  |  |  | 2.28 | 11.85 | 0 | 3.05 | 0
3 | EXT. WALL E |  |  |  |  | 2.28 | 11.85 | 0 | 6.95 | 0
4 | EXT. WALL SE |  |  |  |  | 2.28 | 9.15 | 0 | 8.55 | 0
5 | EXT. WALL S |  |  |  |  | 2.28 | 7.95 | 0 | 9.65 | 0
6 | EXT. WALL SW |  |  |  |  | 2.28 | 9.95 | 0 | 9.35 | 0
7 | EXT. WALL W |  |  |  |  | 2.28 | 13.05 | 0 | 8.15 | 0 |  | CLTD Summer | CLTD Rainy
8 | EXT. WALL NW |  |  |  |  | 2.28 | 12.65 | 0 | 3.85 | 0 |  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
9 | EXT. GLASS N |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
10 | EXT. GLASS NE |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
11 | EXT. GLASS E |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
12 | EXT. GLASS SE |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
13 | EXT. GLASS S |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
14 | EXT. GLASS SW |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
15 | EXT. GLASS W |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
16 | EXT. GLASS NW |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
17 | INT. WALLS. |  |  |  |  | 2.28 | 8.2 | 0 | 3.3 | 0
18 | INT. GLASS. |  |  |  |  | 7.1 | 8.2 | 0 | 3.3 | 0
19 | FLOOR WITHOUT CONDITIONED SPACE BELOW |  |  |  |  | 3.19 | 8.2 | 0 | 3.3 | 0
20 | ROOF EXPOSED |  |  |  |  | 0.7 | 27.65 | 0 | 21.75 | 0
21 | ROOF NON EXPOSED WITHOUT CONDITIONED SPACE ABOVE |  |  |  |  | 3.19 | 8.2 | 0 | 3.3 | 0
22 | ROOF LIGHTS |  |  |  |  | 5.23 | 1.05 | 0 | -3.85 | 0 |  | -1.1 | -1.1 | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
23 | MISC. | [6 empty] | 0 |  | 0
A | TOTAL GAINS AND LOSSES, W. | [6 empty] | 0 |  | 0
SOLAR HEAT GAINS |  |  |  |  | SUMMER |  |  | RAINY
ITEM.NO. | DESCRIPTION |  | AREA, m2 | SHADING COEFFICIENT | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | COOLING LOAD FACTOR | SHGF | HEAT GAIN, W. | Solar time used -> | 6 | 6 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
1 | EXT. GLASS N |  | 0 | 0.7 | 0.73 | 237 | 0 | 0.73 | 101 | 0 |  | 0.73 | 0.73 | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
2 | EXT. GLASS NE |  | 0 | 0.7 | 0.56 | 625 | 0 | 0.56 | 199 | 0 |  | 0.56 | 0.56 | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
3 | EXT. GLASS E |  | 0 | 0.7 | 0.47 | 644 | 0 | 0.47 | 675 | 0 |  | 0.47 | 0.47 | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
4 | EXT. GLASS SE |  | 0 | 0.7 | 0.3 | 284 | 0 | 0.3 | 767 | 0 |  | 0.3 | 0.3 | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
5 | EXT. GLASS S |  | 0 | 0.7 | 0.09 | 126 | 0 | 0.09 | 565 | 0 |  | 0.09 | 0.09 | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
6 | EXT. GLASS SW |  | 0 | 0.7 | 0.07 | 284 | 0 | 0.07 | 767 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
7 | EXT. GLASS W |  | 0 | 0.7 | 0.06 | 644 | 0 | 0.06 | 675 | 0 |  | 0.06 | 0.06 | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
8 | EXT. GLASS NW |  | 0 | 0.7 | 0.07 | 625 | 0 | 0.07 | 199 | 0 |  | 0.07 | 0.07 | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
9 | ROOFLIGHTS. |  | 0 | 0.6 | 0.12 | 864 | 0 | 0.12 | 820 | 0 |  | 0.12 | 0.12 | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
10 | MISC. | [5 empty] | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | TOTAL SOLAR HEAT GAINS, W. | [5 empty] | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BODY GAINS |  |  |  |  | CLF | SENS., W. | LAT., W.
1 | NO. |  | x | 60 | 1 | 0
2 | NO. |  | x | 70 |  |  | 0
C | TOTAL BODY GAIN. |  |  |  |  | 0 | 0
EQUIPMENT GAINS |  |  |  |  | USAGE & DIV FACTOR | CLF | SENS., W. | LAT., W.
1 | LIGHTING. |  | x | 20 | 1 | 1 | 0
2 | SMALL APPLIANCES |  | x | 100 | 0.4 | 1 | 0
3 | LARGE APPLIANCES |  | x | 1000 | 0.4 | 1 | 0
4 | ELECTRICAL PLANTS |  |  |  | 1 | 1 | 0
5 | AREA LOADING LIGHT |  | x |  | 1 | 1 | 0
6 | AREA LOADING POWER |  | x |  | 1 | 1 | 0
7 | MISC. SENSIBLE |  |  |  | 1 | 1 | 0
8 | MISC. LATENT |  |  |  | 1 |  |  | 0
D | TOTAL EQUIPMENT GAINS, W. | [5 empty] | 0 | 0
INFILTRATION GAINS | [6 empty] | SUMMER |  | RAINY
| AREA | HEIGHT | ac/h |  | CMH | CMH | SENS., W. | LAT., W. | SENS., W. | LAT., W.
1 |  |  | 0.5 | + |  | 0 | 0 | 0 | 0 | 0
E | TOTAL INFILTRATION GAINS. | [5 empty] | 0 | 0 | 0 | 0
HEAT GAIN SUMMARY
|  |  |  | SUMMER | RAINY |  |  |  | SUMMER | RAINY
ITEM No. | ITEM |  |  | GAIN, kW. | GAIN, kW.
1 | TRANSMITTANCE. |  |  | 0 | 0 |  | Room S.H.R. (%) |  | #DIV/0! | #DIV/0!
2 | SOLAR. |  |  | 0 | 0 |  | No. of Air Changes per hour |  | #DIV/0! | #DIV/0!
3 | BODY |  |  | 0 | 0 |  | TOUT, BAL (OC) |  | #DIV/0! | #DIV/0!
4 | EQUIPMENT |  |  | 0 | 0 |  | Solar time used for glass load |  | 6 | 6
5 | INFILTRATION. |  |  | 0 | 0
I | TOTAL ROOM SENSIBLE |  |  | 0 | 0
1 | BODY |  |  | 0 | 0
2 | EQUIPMENT. |  |  | 0 | 0
3 | INFILTRATION. |  |  | 0 | 0
II | TOTAL ROOM LATENT |  |  | 0 | 0
III | TOTAL ROOM HEAT LOAD |  |  | 0 | 0
| ROOM SUPPLY AIR TEMP (OC) |  |  | 16.6098 | 16.4169
| PRELIMINARY S.A.V. (m3/s) |  |  | 0 | 0
IV | DUCT GAIN = 1230 x SAV x 1OC (W) |  |  | 0 | 0
V | FAN GAIN (W) |  |  | 10 | 10
| S.A.V. INC. DUCT GAIN & FAN POWER (m3/s) |  |  | 0.0008658 | 0.00084838
| MIN HUMIDITY RATIO REQUIRED FOR SUPPLY AIR |  |  | 0.010542 | 0.010542
| MIXING RATIO (% FRESH AIR) |  |  | 0.1 | 0.1
| COIL BYPASS FACTOR |  |  | 0.15 | 0.15
| TEMPERATURE OF MIXED AIR (OC) |  |  | 27.12 | 26.63
| HUMIDITY RATIO OF MIXED AIR |  |  | 0.011171 | 0.011706
| WADP OF COOLING COIL |  |  | 0.010431 | 0.010336
| TADP OF COOLING COIL (OC) |  |  | 14.755 | 14.6146
| SUPPLY AIR TEMP OF COOLING COIL (OC) |  |  | 16.6098 | 16.4169
VI | COOLING COIL SENSIBLE LOAD (W) |  |  | 11.1927 | 10.6574
VII | COOLING COIL LATENT LOAD (W) |  |  | 1.64 | 2.9723 | AHU DESIGN SUMMARY
VIII | COOLING COIL TOTAL LOAD (W) |  |  | 12.8327 | 13.6297
| COOLING COIL TOTAL LOAD (T.R.) |  |  | 0.0036488 | 0.0038754 | I | COIL LOAD |  | 0.0042629 | Tr
IX | HEATING COIL WATTAGE (kW) |  |  | 0 | 0 | II | AIR HANDLING CAPACITY |  | 3.4286 | CMH
X | BLOWER AIR DELIVERY (CMH) |  |  | 3.1169 | 3.0542 |  | (Both i/c of 10% safety factor)
| BLOWER STATIC (Pa) |  |  | 600 | 600 |  | CFM/Tr |  | 473
| BLOWER MOTOR I/P (kW) |  |  | 0.01 | 0.01 |  | Sq.m/Tr |  | 0

## VALUES
DATA FOR CHENNAI/PUDUCHERRY
I | SHGF FACTORS FOR GLASS
|  | SUMMER |  | RAINY
| DIRECTION | SHGF FOR 12°N & JUNE | SHGC | SHGF FOR 8°N & NOV | SHGC
|  | Btu/(hr.ft^2) | W/m2 | Btu/(hr.ft^2) | W/m2
| N | 75 | 237 | 32 | 101
| NE | 198 | 625 | 63 | 199
| E | 204 | 644 | 214 | 675
| SE | 90 | 284 | 243 | 767
| S | 40 | 126 | 179 | 565
| SW | 90 | 284 | 243 | 767
| W | 204 | 644 | 214 | 675
| NW | 198 | 625 | 63 | 199
| HORIZONTAL | 274 | 864 | 260 | 820
I | CLF FACTORS FOR GLASS
| DIRECTION | SOLAR TIME
|  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| N | 0.73 | 0.66 | 0.65 | 0.73 | 0.8 | 0.86 | 0.89 | 0.89 | 0.86 | 0.82 | 0.75 | 0.78 | 0.91
| NE | 0.56 | 0.76 | 0.74 | 0.58 | 0.37 | 0.29 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
| E | 0.47 | 0.72 | 0.8 | 0.76 | 0.62 | 0.41 | 0.27 | 0.26 | 0.24 | 0.22 | 0.2 | 0.16 | 0.12
| SE | 0.3 | 0.57 | 0.74 | 0.81 | 0.79 | 0.68 | 0.49 | 0.33 | 0.28 | 0.25 | 0.22 | 0.18 | 0.13
| S | 0.09 | 0.16 | 0.23 | 0.38 | 0.58 | 0.75 | 0.83 | 0.8 | 0.68 | 0.5 | 0.35 | 0.27 | 0.19
| SW | 0.07 | 0.11 | 0.14 | 0.16 | 0.19 | 0.22 | 0.38 | 0.59 | 0.75 | 0.83 | 0.81 | 0.69 | 0.45
| W | 0.06 | 0.09 | 0.11 | 0.13 | 0.15 | 0.16 | 0.17 | 0.31 | 0.53 | 0.72 | 0.82 | 0.81 | 0.61
| NW | 0.07 | 0.11 | 0.14 | 0.17 | 0.19 | 0.2 | 0.21 | 0.22 | 0.3 | 0.52 | 0.73 | 0.82 | 0.69
| HORIZONTAL | 0.12 | 0.27 | 0.44 | 0.59 | 0.72 | 0.81 | 0.85 | 0.85 | 0.81 | 0.71 | 0.58 | 0.42 | 0.25
II | CLTD FACTORS FOR ROOF
|  |  | SUMMER |  |  | RAINY
| DIRECTION | SOLAR TIME 6: CLTD FOR ROOF (4" CC with insulation); SOLAR TIME 7: CORRECTION FOR 8°N & JUNE; SOLAR TIME 8: COLOUR CORRECTION; SOLAR TIME 9: CLTD FOR ROOF; SOLAR TIME 10: CORRECTION FOR 8°N & NOV; SOLAR TIME 11: COLOUR CORRECTION; SOLAR TIME 12: CLTD FOR ROOF
|  | °F | °F |  | °C | °F |  | °C
| HORIZONTAL | SOLAR TIME 6: 53; SOLAR TIME 7: -2; SOLAR TIME 8: 0.9; SOLAR TIME 9: 25.5; SOLAR TIME 10: -4; SOLAR TIME 11: 0.9; SOLAR TIME 12: 24.5
III | CLTD FACTORS FOR WALL
|  |  | SUMMER |  |  | RAINY
| DIRECTION | SOLAR TIME 6: CLTD FOR WALL (8" BRICK); SOLAR TIME 7: CORRECTION FOR 8°N & JUNE; SOLAR TIME 8: COLOUR CORRECTION; SOLAR TIME 9: CLTD FOR WALL; SOLAR TIME 10: CORRECTION FOR 8°N & NOV; SOLAR TIME 11: COLOUR CORRECTION; SOLAR TIME 12: CLTD FOR WALL
|  | °F | °F |  | °C | °F |  | °C
| N | SOLAR TIME 6: 15; SOLAR TIME 7: 9; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.3; SOLAR TIME 10: -3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 4.7
| NE | SOLAR TIME 6: 21; SOLAR TIME 7: 4; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.7; SOLAR TIME 10: -6; SOLAR TIME 11: 0.7; SOLAR TIME 12: 5.8
| E | SOLAR TIME 6: 27; SOLAR TIME 7: -2; SOLAR TIME 8: 0.7; SOLAR TIME 9: 9.7; SOLAR TIME 10: -2; SOLAR TIME 11: 0.7; SOLAR TIME 12: 9.7
| SE | SOLAR TIME 6: 26; SOLAR TIME 7: -8; SOLAR TIME 8: 0.7; SOLAR TIME 9: 7; SOLAR TIME 10: 3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 11.3
| S | SOLAR TIME 6: 22; SOLAR TIME 7: -7; SOLAR TIME 8: 0.7; SOLAR TIME 9: 5.8; SOLAR TIME 10: 10; SOLAR TIME 11: 0.7; SOLAR TIME 12: 12.4
| SW | SOLAR TIME 6: 28; SOLAR TIME 7: -8; SOLAR TIME 8: 0.7; SOLAR TIME 9: 7.8; SOLAR TIME 10: 3; SOLAR TIME 11: 0.7; SOLAR TIME 12: 12.1
| W | SOLAR TIME 6: 30; SOLAR TIME 7: -2; SOLAR TIME 8: 0.7; SOLAR TIME 9: 10.9; SOLAR TIME 10: -2; SOLAR TIME 11: 0.7; SOLAR TIME 12: 10.9
| NW | SOLAR TIME 6: 23; SOLAR TIME 7: 4; SOLAR TIME 8: 0.7; SOLAR TIME 9: 10.5; SOLAR TIME 10: -6; SOLAR TIME 11: 0.7; SOLAR TIME 12: 6.6
IV | CLTD FACTORS FOR GLASS
| DIRECTION | SOLAR TIME 6: SOLAR TIME
|  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| ALL (°F) | -2 | -2 | 0 | 2 | 4 | 7 | 9 | 12 | 13 | 14 | 14 | 13 | 12
| ALL (°C) | -1.1 | -1.1 | 0 | 1.1 | 2.2 | 3.9 | 5 | 6.7 | 7.2 | 7.8 | 7.8 | 7.2 | 6.7
V | TYPICAL VALUES
ACTIVITY LEVEL
| Degree of Activity | SOLAR TIME 6: Typical Application; SOLAR TIME 7: Average Metabolic Rate - male adult (W); SOLAR TIME 8: Room Dry Bulb Temperature (oC)
|  |  |  | 28 |  | 27 |  | 26 |  | 24 |  | 22 |  | 20
Heat (W)
|  |  |  | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat.
| Seated at rest | Cinema, theater, school | 100 | 50 | 50 | 55 | 45 | 60 | 40 | 67 | 33 | 72 | 28 | 79 | 21
| Seated, very light work | Computer working | 120 | 50 | 70 | 55 | 65 | 60 | 60 | 70 | 50 | 78 | 42 | 84 | 36
| Office work | Hotel reception, cashier | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
| Standing, walking slowly | Laboratory work | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
| Walking, seated |  | 150 | 53 | 97 | 58 | 92 | 64 | 86 | 76 | 74 | 84 | 66 | 90 | 60
| Moderate work | Servant, hair dresser | 160 | 55 | 105 | 60 | 100 | 68 | 92 | 80 | 80 | 90 | 70 | 98 | 62
| Light bench work | Mechanical production | 220 | 55 | 165 | 52 | 158 | 70 | 150 | 85 | 135 | 100 | 120 | 115 | 105
| Moderate Dancing | Party | 250 | 62 | 188 | 70 | 180 | 78 | 172 | 94 | 156 | 110 | 140 | 125 | 125
| Fast walking | Mountain walking | 300 | 80 | 220 | 88 | 212 | 96 | 204 | 110 | 190 | 130 | 170 | 145 | 155
| Heavy work | Athletics | 430 | 132 | 298 | 138 | 292 | 144 | 286 | 154 | 276 | 170 | 260 | 188 | 242