## S - Fan noise calculator
FAN NOISE

Type of fan	4	4, Centrifugal – Forward Curved
Q	4760	CMH
P	500	Pa
Q	2800	CFM
P	2.01	“ H2O
eff	0.8
Cn	4.0

Octave Band	2	3	4	5	6	7
Mid Frequency (Hz)	125	250	500	1000	2000	4000
Cn	38	38	34	28	24	21
Lw (dB)	83	83	79	73	69	66

Lw = Kw + 10 log(Q) + 20 Log(P) + BFI + Cn

Lw= sound power level (dB)
Kw = specific sound power level depending on the type of fan (see Fig 9-3), from
empirical data provided by fan manufacturer
Q = volume flow rate (cfm)
P = total pressure (inches of H20)
BFI = Blade Frequency Increment = correction for pure tone produced by the blade
passing frequency (bpf) from Fig 9-3, add this correction only to the octave band
whose center frequency is closest to the blade passing frequency.
bpf= blade passing frequency = #of blades × RPM/60 (Hz)
Cn = efficiency correction (because fans that are operated off their optimum flow
conditions get noisier)

## P - Plenum - S
PLENUM INSERTION LOSS – S (ASHRAE Applications, 48.2.4)

Type of lining	3	3, 25 mm, 48 kg/m3
l	4.3	m	(Plenum length)
w	0.8	m	(Plenum width)
h	0.8	m	(Plenum height)
V	2.8	cum.m	(Plenum volume)
a	0.5	m	(Inlet width)
b	0.5	m	(Inlet height)
fc	343		(Critical frequency)
r	1.3	m	(Distance between inlet and outlet)
Sout	0.175	sq.m	(Area of plenum outlet)
S	14.44	sq.m	(Total area of duct minus openings)
Q	2		(Directionality factor: 2 for opening near center, 4 for opening near corner)
Offset angle	4	4, 30	(Sound absorbtion coefficient)

Octave Band	2	3	4	5	6	7
Mid Frequency (Hz)	125	250	500	1000	2000	4000
αa	0.11	0.28	0.68	0.9	0.93	0.96
OAE	-2	3	2	4	4	5
Af	0.4	0.4	0.2	0	0	0
We	2	5	9	0	0	0

TL (dB)	20	20	16	19	19	20

## P - Plenum - R1
PLENUM INSERTION LOSS – R1 (ASHRAE Applications, 48.2.4)

Type of lining	3	3, 25 mm, 48 kg/m3
l	4	m	(Plenum length)
w	2.4	m	(Plenum width)
h	1	m	(Plenum height)
V	9.6	cum.m	(Plenum volume)
a	0.6	m	(Inlet width)
b	0.6	m	(Inlet height)
fc	286		(Critical frequency)
r	3.3	m	(Distance between inlet and outlet)
Sout	0.48	sq.m	(Area of plenum outlet)
S	31.16	sq.m	(Total area of duct minus openings)
Q	2		(Directionality factor: 2 for opening near center, 4 for opening near corner)
Offset angle	7	7, 90	(Sound absorbtion coefficient)

Octave Band	2	3	4	5	6	7
Mid Frequency (Hz)	125	250	500	1000	2000	4000
αa	0.11	0.28	0.68	0.9	0.93	0.96
OAE	0	0	0	0	0	0
Af	0.4	0.4	0.2	0	0	0
We	2	5	9	0	0	0

TL (dB)	20	20	16	19	20	20

## P - Plenum - R2
PLENUM INSERTION LOSS – R2 (ASHRAE Applications, 48.2.4)

Type of lining	3	3, 25 mm, 48 kg/m3
l	7	m	(Plenum length)
w	1.8	m	(Plenum width)
h	1.3	m	(Plenum height)
V	16.4	cum.m	(Plenum volume)
a	1.2	m	(Inlet width)
b	0.4	m	(Inlet height)
fc	143		(Critical frequency)
r	6.2	m	(Distance between inlet and outlet)
Sout	0.48	sq.m	(Area of plenum outlet)
S	47.12	sq.m	(Total area of duct minus openings)
Q	4		(Directionality factor: 2 for opening near center, 4 for opening near corner)
Offset angle	6	6, 45	(Sound absorbtion coefficient)

Octave Band	2	3	4	5	6	7
Mid Frequency (Hz)	125	250	500	1000	2000	4000
αa	0.11	0.28	0.68	0.9	0.93	0.96
OAE	-6	19	5	9	10	12
Af	0.4	0.4	0.2	0	0	0
We	2	5	9	0	0	0

TL (dB)	20	31	24	32	34	37

## Calculation sheet
	ROOM ACCOUSTIC CALCULATIONS

	Octave Band	Dia	W	H	t	L/#	2	3	4	5	6	7	ILS2	ILS3	ILS4	ILS5	ILS6	ILS7
	Mid Frequency (Hz)	(m)	(m)	(m)	(mm)	(m)	125	250	500	1000	2000	4000

I	Supply discharge path
	Terminal discharge from Fan					83	83	79	73	69	66
	Environmental Adjustment Factor					2	1	0	0	0	0
	Lined rectangular duct		0.5	0.5	25	1	0.0	0.0	0.0	0.0	8.7	6.7
	Plenum – S					20.0	20.0	15.8	18.9	19.0	20.1
	Branch power division	0.5	1				3.0	3.0	3.0	3.0	3.0	3.0
	Lined rectangular duct		0.7	0.25	25	2	2.1	4.5	11.3	24.0	22.6	16.2
	Branch power division	0.33	1				4.8	4.8	4.8	4.8	4.8	4.8
	Lined square elbow		0.5	0.3	25	1	1	6	11	10	10	10
	End reflection loss (Flush terminated)	0.339	0.3	0.3			6.3	2.6	0.8	0.2	0.1	0.0
	Space Effect (Multiple outlets)	12	2.8	6			4.1	5.0	5.9	6.8	7.7	8.6

	Lw (dB)					40	36	26	5	0	0	9310.89760637262	4038.29311872221	442.784935951296	3.42146564435092	1	1

II	Supply duct breakout path
	Terminal discharge from Fan					83	83	79	73	69	66
	Environmental Adjustment Factor					2	1	0	0	0	0
	Lined rectangular duct		0.5	0.5	25	1	0.0	0.0	0.0	0.0	8.7	6.7
	Plenum					20.0	20.0	15.8	18.9	19.0	20.1
	Branch power division	0.5	1				3.0	3.0	3.0	3.0	3.0	3.0
	Lined rectangular duct		0.7	0.25	25	2	2.1	4.5	11.3	24.0	22.6	16.2
	Rectangular duct breakout		0.7	0.25		3.2	6.6	9.6	12.6	15.6	19.6	25.6
	Ceiling Effect (Gypsum board tiles)					16	18	18	21	22	22

	Lw (dB)					33	27	18	0	0	0	2130.13280971711	484.502402537813	68.7348911310996	1	1	1

III	Outlet Generated
	Diffuser generated noise (NC15)					46	39	32	27	24	22
	Environmental Adjustment Factor					2	1	0	0	0	0
	Space Effect (Multiple outlets)	12	2.8	6			4.1	5.0	5.9	6.8	7.7	8.6

	Lw (dB)					40	33	26	20	16	13	9830.4026760055	2005.68307263366	409.216663898016	105.110066730311	42.7893129351213	21.9293780396765

IV	Return air discharge path
	Terminal discharge from Fan					83	83	79	73	69	66
	Environmental Adjustment Factor					2	1	0	0	0	0
	Plenum – R1					20.0	20.0	16.1	19.2	19.7	20.2
	Plenum – R2					20.0	31.3	24.2	32.3	33.9	36.6
	Branch power division	0.20	1				7.0	7.0	7.0	7.0	7.0	7.0
	End reflection loss (Flush terminated)	0.339	0.3	0.3			6.3	2.6	0.8	0.2	0.1	0.0
	Space Effect (Multiple outlets)	15	2.8	5			4.4	5.3	6.2	7.1	8.0	8.9

	Lw (dB)					23	16	25	7	0	0	215.438498252184	38.1843405758559	295.455609482528	5.21294527063908	1.08221814286738	1

V	Return air radiated path
	Terminal discharge from Fan					83	83	79	73	69	66
	Environmental Adjustment Factor					2	1	0	0	0	0
	Plenum – R1					20.0	20.0	16.1	19.2	19.7	20.2
	Plenum – R2					20.0	31.3	24.2	32.3	33.9	36.6
	Ceiling Effect (Gypsum board tiles)					16	18	18	21	22	22

	Lw (dB)					25	13	21	0	0	0	316.227766016838	18.5457733037518	117.148897985932	1.11337934215913	1	1

Σ	NET Lw (dB)					43	38	31	21	17	14
	NC					26
Octave Band
Sound Power Level, dB

## Constants
Sound Constants - ARI 885 -90 and -98

	Band Constants					Equation
Octave Band	2	3	4	5	6	7
Mid Frequency, Hz	125	250	500	1000	2000	4000
NC Drivers					NC= M1*Band Spl+ Intcpt
Intcpt	-31.6	-18.9	-8.5	-2.2	1	3.1
M1	1.28	1.18	1.09	1.02	1.00	0.98

Lined Duct
Constants	125	250	500	1000	2000	4000		dB/ft = 10^C1 * p/a^C2 * t^C3
C1	-0.865	-0.582	-0.0121	0.298	0.089	0.0649		where :
C2	0.723	0.826	0.487	0.513	0.862	0.629		p/a = 2*(Width+Height)/(Width*Height)*12, in inches					Application Reductions
C3	0.375	0.975	0.868	0.317	0	0		t = lining thickness, in.					0	0	0	0	0	0

Flex Duct
Constants	125	250	500	1000	2000	4000		IL, by Band = (C1+C2*Dia+C3*Dia^2) + ((C4+C5*Dia+C6*Dia^2)*Length)
C1	3.601052	-2.023119	1.533116	24.45197	26.15493	25.06003		Diameter in inches, Length in feet
C2	-0.1250605	1.276239	1.407587	-2.844882	-2.885191	-4.0431
C3	-0.006339209	-0.08211643	-0.08316611	0.08517541	0.08842091	0.1626905
C4	0.4852413	-0.6914328	1.948206	0.8380425	1.702466	0.2239686
C5	0.07578726	0.4378392	0.06271727	0.3254958	0.1615714	0.344374
C6	-0.005221358	-0.02081597	-0.005056188	-0.01468515	-0.009956212	-0.020039

ARI 885-98 / Radiated, combined ceiling plenum/space effect
Ceiling/Plenum Effect Attenuation Values, Radiated sound					Table from ARI standard
Tile Type	125	250	500	1000	2000	4000
1, Mineral Fiber	16	18	20	26	31	36
2, Mineral Fiber	15	17	19	25	30	33
3, Glass Fiber	16	15	17	17	18	19
4, Glass Fiber	17	18	21	25	29	35
5, Glass Fiber, TL Backed	17	18	22	27	32	39
6, Gypsym Board Tiles	16	18	18	21	22	22
7, Solid Gypsum Board	21	25	25	27	27	28
8, Solid Gypsum Board	23	27	27	29	29	30
9, Double Gypsum Board	27	31	31	33	33	34
10, Double Gypsum Board	29	33	33	35	35	36
11, Concealed Spline	23	24	24	29	33	34

ARI 885-90 / ceiling plenum effect
Ceiling/Plenum Effect Attenuation Values, Radiated sound					Add to space effect for ARI 885-90 calculations
Tile Type	125	250	500	1000	2000	4000
1, Mineral Fiber	9	10	12	14	15	15
2, Glass Fiber	8	8	8	10	10	14
3, Solid Gypsum Board	15	21	25	27	26	27

Space Effect, Point Source					Shultz equation
Log Distance, ft.	10					Room SPL = Sound Power less (10 * Log(Distance) + 5 * Log(Volume)+ 3 * Log(Freq[I]) - 25)
Log Room Volume, CuFt	5
Log Frequency, Hz	3
Constant	25

Environmental Adjustment Factor
Standard referenced	125	250	500	1000	2000	4000
ARI 885-90	3	2	1	1	1	1
ARI 885-98	2	1	0	0	0	0

Specific sound power level
Type	125	250	500	1000	2000	4000
1, Centrifugal – Aerofoil	35	34	32	31	26	18
2, Centrifugal – Backward Curved	35	34	32	31	26	18
3, Centrifugal – Radial	45	43	43	38	33	30
4, Centrifugal – Forward Curved	38	38	34	28	24	21
5, Axial – Vaneaxial	39	41	42	40	37	35
6, Axial – Tubeaxial	42	46	44	42	40	37
7, Axial – Propeller	48	49	47	45	45	43
8, Axial – Tubular centrifugal	43	43	38	37	32	28

Sound absorbtion coefficient
Type	125	250	500	1000	2000	4000
1, Concrete	0.01	0.01	0.02	0.02	0.02	0.03
2, Bare sheet metal	0.04	0.04	0.05	0.05	0.05	0.07
3, 25 mm, 48 kg/m3	0.11	0.28	0.68	0.9	0.93	0.96
4, 50 mm, 48 kg/m3	0.17	0.86	1	1	1	1
5, 100 mm, 48 kg/m3	0.84	1	1	1	1	0.97

Area Coefficient, Wall effect
Type	125	250	500	1000	2000	4000
1, Af, V<1.5 cum.m	2.4	2.2	1.1	0	0	0
2, Af, V>1.5 cum.m	0.4	0.4	0.2	0	0	0
1, Concrete	0	0	0	0	0	0
2, Bare sheet metal	0	0	0	0	0	0
3, We, 25 mm, 40 kg/m3	2	5	9	0	0	0
4, We, 50 mm, 40 kg/m3	3	9	13	0	0	0
5, We, 100 mm, 40 kg/m3	6	13	12	0	0	0

Offset angle/ elbow effects
Type	125	250	500	1000	2000	4000
f< fc
1, 0	0	0	0	0	0	0
2, 15	1	1	1	0	0	0
3, 22.5	0	2	3	0	0	0
4, 30	-2	3	6	0	0	0
5, 37.5	-4	5	10	0	0	0
6, 45	-6	7	15	0	0	0
7, 90	0	0	2	2	2	2
f< fc
1, 0	0	0	0	0	0	0
2, 15	0	2	0	1	1	0
3, 22.5	0	4	1	2	2	2
4, 30	0	8	2	4	4	5
5, 37.5	0	13	4	6	7	8
6, 45	0	19	5	9	10	12
7, 90	3	-3	0	0	0	0

Rectanglular duct breakout
Type	125	250	500	1000	2000	4000
[300 x 300]	24	27	30	33	36	41
[300 x 600]	22	25	28	31	35	41
[300 x 1200]	22	25	28	31	37	43
[600 x 600]	23	26	29	32	37	43
[600 x 1200]	23	26	29	31	39	45
[1200 x 1200]	24	27	30	35	41	45
[1200 x 2400]	22	25	29	35	41	45
Minimum	22	25	28	31	35	41

## NC_Source
WRITTEN BY: TARSHA L. SIMON					DATE: Jan 17, 1991
MODIFIED BY: D Int-Hout, 2/95
NCPLOT					RC Data

		-2			50
		-1			45
	32	0		0	40
NC15	63	1	47	1	35
	125	2	36	2	30
	250	3	29	3	25
	500	4	22	4	20
	1000	5	17	5	15
	2000	6	14	6	10
	4000	7	12	7	5
		8			0

		-1			50
	32	0			45
NC20	63	1	51		40
	125	2	40		35
	250	3	33		30
	500	4	26		25
	1000	5	22		20
	2000	6	19		15
	4000	7	17		10
		8			5

		-1			55
	32	0			50
NC25	63	1	54		45
	125	2	44		40
	250	3	37		35
	500	4	31		30
	1000	5	27		25
	2000	6	24		20
	4000	7	22		15
		8			10

		-1			60
		0			55
NC30	63	1	57		50
	125	2	48		45
	250	3	41		40
	500	4	35		35
	1000	5	31		30
	2000	6	29		25
	4000	7	28		20
		8			15

		-1			65
		0			60
NC35	63	1	60		55
	125	2	52		50
	250	3	45		45
	500	4	40		40
	1000	5	36		35
	2000	6	34		30
	4000	7	33		25
		8			20

		-1			70
		0			65
NC40	63	1	64		60
	125	2	56		55
	250	3	50		50
	500	4	45		45
	1000	5	41		40
	2000	6	39		35
	4000	7	38		30
		8			25

		-1			75
		0			70
NC45	63	1	67		65
	125	2	60		60
	250	3	54		55
	500	4	49		50
	1000	5	46		45
	2000	6	44		40
	4000	7	43		35
		8			30

		-1			80
		0			75
NC50	63	1	71		70
	125	2	64		65
	250	3	58		60
	500	4	54		55
	1000	5	51		50
	2000	6	49		45
	4000	7	48		40
		8			35

		-1			85
		0			80
NC55	63	1	74		75
	125	2	67		70
	250	3	62		65
	500	4	58		60
	1000	5	56		55
	2000	6	54		50
	4000	7	53		45
		8			40

		-1			90
		0			85
NC60	63	1	77		80
	125	2	71		75
	250	3	67		70
	500	4	63		65
	1000	5	61		60
	2000	6	59		55
	4000	7	58		50
		8			45

		-1			95
		0			90
NC65	63	1	80		85
	125	2	75		80
	250	3	71		75
	500	4	68		70
	1000	5	66		65
	2000	6	64		60
	4000	7	63		55
		8			50

		-1	78		78
		0	58		58
HEARING THRESHOLD		1	36		36
		2	22		22
		3	13		13
		4	8		1
		5
		6
		7
		8