## Naturally Ventillated
DESIGN OF VENTILLATION OPENINGS FOR TRANFORMER
| Location | MAIN SS
| Transformer rating | 630kVA, Eff.Lvl.2
| Transformer loss at full load | 5300 | W
| Ambient Temperature | 35 | °C
| Room temperature | 45 | °C
| Air movement required for heat dessipation | 0.43089 | CMS
|  | 1551.2195 | CMH
| Inlet path resistance | 5
| Outlet path resistance | 5.5
| Ratio Inlet/Outlet | 0.90909
| Height between openings | 3
| Inlet Area | 0.91511 | sq.m
| Outlet Area | 1.0066 | sq.m

## Reference
Resistance Values
Element | Path
Acceleration | 1
Right angle bend | 1.5
Rounded bend | 1
Slow change of direction | 0 – 0.6
Wire screen | 0.5 – 1
Slats | 2.5 – 3.5
Cross section widening (1:2 to 1:10) | 0.25 – 0.9
DP = 0.5*ρ*Σ(V2*Cv) = 0.5*ρ*Q/A1*Σ(R1+R2*m2) where m=A1/A2