## 2x2 panel
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 300
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 4.9 | m
Width (W) = | 5.5 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 2.7 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 1.85 | m |  |  | 116 | 0 | 119 | 119 | 119 | 119 | 116 | 116 | 116 | 116 | 111 | 111 | 111 | 106 | 106 | 106 | 102 | 102 | 102 | 100
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 104 | 1 | 110 | 106 | 102 | 99 | 108 | 104 | 101 | 98 | 100 | 97 | 94 | 96 | 94 | 92 | 92 | 91 | 89 | 87
|  |  | Lamp Wattage = | 30 | 92 | 2 | 101 | 94 | 88 | 83 | 99 | 92 | 87 | 82 | 89 | 84 | 80 | 86 | 82 | 78 | 83 | 80 | 77 | 75
|  |  | Lamp Flux = | 3000 | 82 | 3 | 93 | 84 | 77 | 71 | 91 | 82 | 76 | 70 | 79 | 74 | 69 | 77 | 72 | 68 | 74 | 70 | 67 | 65
Room Index (K ) = | 1.4007 |  |  |  | 74 | 4 | 86 | 75 | 67 | 61 | 84 | 74 | 66 | 61 | 71 | 65 | 60 | 69 | 64 | 59 | 67 | 62 | 58 | 56
Utilization F. (Uf) = | 1.04 |  | Maintenance Factor (Mf) = | 0.722 | 67 | 5 | 80 | 68 | 59 | 53 | 78 | 67 | 59 | 53 | 65 | 58 | 52 | 63 | 57 | 52 | 61 | 56 | 51 | 49
No. of Luminaries required (N) = |  |  | 3.5891 |  | 60 | 6 | 74 | 61 | 53 | 47 | 72 | 60 | 53 | 47 | 59 | 52 | 46 | 57 | 51 | 46 | 56 | 50 | 46 | 44
[5 empty] | 55 | 7 | 69 | 56 | 48 | 42 | 67 | 55 | 47 | 42 | 54 | 47 | 41 | 52 | 46 | 41 | 51 | 45 | 41 | 39
No. of Luminaries along length (Ng) = |  |  | 1.7882 | 4 | 51 | 8 | 64 | 51 | 43 | 38 | 63 | 51 | 43 | 38 | 49 | 42 | 37 | 48 | 42 | 37 | 47 | 41 | 37 | 35
No. of Luminaries along breadth (Nc) = |  |  | 2.0071 | 2 | 47 | 9 | 60 | 47 | 39 | 34 | 59 | 47 | 39 | 34 | 45 | 39 | 34 | 44 | 38 | 34 | 43 | 38 | 34 | 32
[5 empty] | 43 | 10 | 56 | 44 | 36 | 31 | 55 | 43 | 36 | 31 | 42 | 35 | 31 | 41 | 35 | 31 | 40 | 35 | 31 | 29
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 669
Energy Density (W/m^2) = |  |  |  | 8.9054
Space to Height Ratio (SHR) = |  | (<1.5) |  | 0.99212
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95

## Batten
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 250
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 40 | m
Width (W) = | 6 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 4 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 3.15 | m |  |  | 114 | 0 | 117 | 117 | 117 | 117 | 114 | 114 | 114 | 114 | 106 | 106 | 106 | 100 | 100 | 100 | 94 | 94 | 94 | 91
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 96 | 1 | 105 | 99 | 94 | 90 | 101 | 96 | 91 | 87 | 90 | 86 | 83 | 84 | 81 | 78 | 79 | 77 | 74 | 72
|  |  | Lamp Wattage = | 30 | 83 | 2 | 95 | 86 | 78 | 72 | 91 | 83 | 76 | 70 | 78 | 72 | 67 | 73 | 68 | 64 | 68 | 64 | 61 | 58
|  |  | Lamp Flux = | 3000 | 72 | 3 | 86 | 75 | 66 | 59 | 83 | 72 | 64 | 58 | 68 | 61 | 55 | 64 | 58 | 53 | 60 | 55 | 51 | 48
Room Index (K ) = | 1.6563 |  |  |  | 64 | 4 | 79 | 66 | 56 | 49 | 75 | 64 | 55 | 48 | 60 | 53 | 47 | 56 | 50 | 45 | 53 | 48 | 43 | 41
Utilization F. (Uf) = | 0.83 |  | Maintenance Factor (Mf) = | 0.722 | 57 | 5 | 72 | 59 | 49 | 42 | 69 | 57 | 48 | 42 | 54 | 46 | 40 | 51 | 44 | 39 | 48 | 42 | 38 | 35
No. of Luminaries required (N) = |  |  | 33.3745 |  | 51 | 6 | 66 | 53 | 43 | 37 | 64 | 51 | 42 | 36 | 48 | 41 | 35 | 46 | 39 | 34 | 43 | 37 | 33 | 31
[5 empty] | 46 | 7 | 62 | 48 | 39 | 32 | 59 | 46 | 38 | 32 | 44 | 36 | 31 | 42 | 35 | 30 | 39 | 34 | 29 | 27
No. of Luminaries along length (Ng) = |  |  | 14.9163 | 4 | 42 | 8 | 57 | 43 | 35 | 29 | 55 | 42 | 34 | 28 | 40 | 33 | 27 | 38 | 32 | 27 | 36 | 30 | 26 | 24
No. of Luminaries along breadth (Nc) = |  |  | 2.2374 | 2 | 39 | 9 | 53 | 40 | 31 | 26 | 52 | 39 | 31 | 25 | 37 | 30 | 25 | 35 | 29 | 24 | 33 | 28 | 23 | 21
[5 empty] | 36 | 10 | 50 | 37 | 29 | 23 | 48 | 36 | 28 | 23 | 34 | 27 | 22 | 32 | 26 | 22 | 31 | 25 | 21 | 19
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 60
Energy Density (W/m^2) = |  |  |  | 1
Space to Height Ratio (SHR) = |  | (<1.5) |  | 1.7388
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95

## Downlighter Surface
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 300
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 9 | m
Width (W) = | 6 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 3 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 2.15 | m |  |  | 116 | 0 | 119 | 119 | 119 | 119 | 116 | 116 | 116 | 116 | 111 | 111 | 111 | 106 | 106 | 106 | 102 | 102 | 102 | 100
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 101 | 1 | 108 | 104 | 99 | 95 | 106 | 101 | 97 | 94 | 97 | 94 | 91 | 93 | 90 | 88 | 89 | 87 | 85 | 83
|  |  | Lamp Wattage = | 30 | 88 | 2 | 98 | 90 | 83 | 77 | 96 | 88 | 82 | 76 | 85 | 79 | 74 | 81 | 77 | 73 | 78 | 74 | 71 | 69
|  |  | Lamp Flux = | 3000 | 77 | 3 | 90 | 79 | 71 | 64 | 87 | 77 | 70 | 63 | 74 | 68 | 62 | 72 | 66 | 61 | 69 | 64 | 60 | 58
Room Index (K ) = | 1.6744 |  |  |  | 68 | 4 | 82 | 70 | 61 | 54 | 80 | 68 | 60 | 54 | 66 | 59 | 53 | 64 | 57 | 52 | 61 | 56 | 51 | 49
Utilization F. (Uf) = | 0.88 |  | Maintenance Factor (Mf) = | 0.722 | 61 | 5 | 75 | 62 | 53 | 46 | 73 | 61 | 53 | 46 | 59 | 51 | 46 | 57 | 50 | 45 | 55 | 49 | 45 | 42
No. of Luminaries required (N) = |  |  | 8.4991 |  | 55 | 6 | 70 | 56 | 47 | 40 | 68 | 55 | 46 | 40 | 53 | 46 | 40 | 52 | 45 | 40 | 50 | 44 | 39 | 37
[5 empty] | 50 | 7 | 64 | 51 | 42 | 36 | 63 | 50 | 42 | 36 | 48 | 41 | 35 | 47 | 40 | 35 | 46 | 39 | 35 | 33
No. of Luminaries along length (Ng) = |  |  | 3.5705 | 4 | 46 | 8 | 60 | 46 | 38 | 32 | 58 | 46 | 37 | 32 | 44 | 37 | 31 | 43 | 36 | 31 | 42 | 36 | 31 | 29
No. of Luminaries along breadth (Nc) = |  |  | 2.3804 | 2 | 42 | 9 | 56 | 42 | 34 | 29 | 55 | 42 | 34 | 28 | 41 | 33 | 28 | 40 | 33 | 28 | 39 | 32 | 28 | 26
[5 empty] | 39 | 10 | 52 | 39 | 31 | 26 | 51 | 39 | 31 | 26 | 38 | 31 | 26 | 37 | 30 | 26 | 36 | 30 | 25 | 24
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 282
Energy Density (W/m^2) = |  |  |  | 4.4444
Space to Height Ratio (SHR) = |  | (<1.5) |  | 1.2084
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95

## Downlighter Recessed
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 250
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 12 | m
Width (W) = | 7 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 6 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 5.15 | m |  |  | 107 | 0 | 109 | 109 | 109 | 109 | 107 | 107 | 107 | 107 | 102 | 102 | 102 | 98 | 98 | 98 | 94 | 94 | 94 | 92
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 96 | 1 | 102 | 98 | 95 | 92 | 99 | 96 | 93 | 90 | 92 | 90 | 87 | 89 | 87 | 85 | 85 | 84 | 82 | 81
|  |  | Lamp Wattage = | 20 | 86 | 2 | 94 | 88 | 82 | 78 | 92 | 86 | 81 | 77 | 83 | 79 | 75 | 80 | 76 | 73 | 77 | 74 | 72 | 70
|  |  | Lamp Flux = | 2000 | 77 | 3 | 87 | 78 | 72 | 67 | 85 | 77 | 71 | 66 | 74 | 69 | 65 | 72 | 68 | 64 | 70 | 66 | 63 | 61
Room Index (K ) = | 0.85846 |  |  |  | 69 | 4 | 80 | 71 | 64 | 58 | 78 | 69 | 63 | 58 | 67 | 62 | 57 | 65 | 60 | 56 | 63 | 59 | 56 | 54
Utilization F. (Uf) = | 0.96 |  | Maintenance Factor (Mf) = | 0.722 | 63 | 5 | 74 | 64 | 57 | 51 | 73 | 63 | 56 | 51 | 61 | 55 | 50 | 59 | 54 | 50 | 58 | 53 | 49 | 48
No. of Luminaries required (N) = |  |  | 15.1489 |  | 57 | 6 | 69 | 58 | 51 | 45 | 68 | 57 | 50 | 45 | 56 | 50 | 45 | 54 | 49 | 45 | 53 | 48 | 44 | 42
[5 empty] | 52 | 7 | 64 | 53 | 46 | 41 | 63 | 52 | 46 | 41 | 51 | 45 | 40 | 50 | 44 | 40 | 49 | 44 | 40 | 38
No. of Luminaries along length (Ng) = |  |  | 5.096 | 4 | 48 | 8 | 60 | 49 | 42 | 37 | 59 | 48 | 41 | 37 | 47 | 41 | 36 | 46 | 40 | 36 | 45 | 40 | 36 | 34
No. of Luminaries along breadth (Nc) = |  |  | 2.9727 | 2 | 45 | 9 | 57 | 45 | 38 | 33 | 55 | 45 | 38 | 33 | 44 | 37 | 33 | 43 | 37 | 33 | 42 | 37 | 33 | 31
[5 empty] | 41 | 10 | 53 | 42 | 35 | 31 | 52 | 41 | 35 | 30 | 40 | 34 | 30 | 40 | 34 | 30 | 39 | 34 | 30 | 29
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 132
Energy Density (W/m^2) = |  |  |  | 1.9048
Space to Height Ratio (SHR) = |  | (<1.5) |  | 0.6292
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95

## Suspended WB
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 300
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 9 | m
Width (W) = | 6 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 3 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 2.15 | m |  |  | 116 | 0 | 119 | 119 | 119 | 119 | 116 | 116 | 116 | 116 | 111 | 111 | 111 | 106 | 106 | 106 | 102 | 102 | 102 | 100
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 107 | 1 | 113 | 109 | 107 | 104 | 110 | 107 | 105 | 102 | 103 | 101 | 99 | 99 | 98 | 96 | 96 | 95 | 93 | 92
|  |  | Lamp Wattage = | 30 | 98 | 2 | 106 | 100 | 95 | 92 | 104 | 98 | 94 | 90 | 95 | 92 | 88 | 92 | 89 | 87 | 89 | 87 | 85 | 83
|  |  | Lamp Flux = | 3000 | 90 | 3 | 99 | 92 | 86 | 81 | 97 | 90 | 85 | 81 | 88 | 83 | 79 | 85 | 81 | 78 | 83 | 80 | 77 | 75
Room Index (K ) = | 1.6744 |  |  |  | 83 | 4 | 93 | 84 | 78 | 73 | 91 | 83 | 77 | 72 | 81 | 76 | 71 | 79 | 74 | 71 | 77 | 73 | 70 | 68
Utilization F. (Uf) = | 0.98 |  | Maintenance Factor (Mf) = | 0.722 | 76 | 5 | 87 | 77 | 71 | 66 | 85 | 76 | 70 | 65 | 75 | 69 | 65 | 73 | 68 | 64 | 71 | 67 | 63 | 62
No. of Luminaries required (N) = |  |  | 7.6319 |  | 70 | 6 | 82 | 71 | 64 | 59 | 80 | 70 | 64 | 59 | 69 | 63 | 59 | 67 | 62 | 58 | 66 | 61 | 58 | 56
[5 empty] | 65 | 7 | 77 | 66 | 59 | 54 | 75 | 65 | 58 | 54 | 64 | 58 | 53 | 62 | 57 | 53 | 61 | 56 | 53 | 51
No. of Luminaries along length (Ng) = |  |  | 3.3835 | 4 | 60 | 8 | 72 | 61 | 54 | 49 | 71 | 60 | 54 | 49 | 59 | 53 | 49 | 58 | 53 | 49 | 57 | 52 | 48 | 47
No. of Luminaries along breadth (Nc) = |  |  | 2.2556 | 2 | 56 | 9 | 68 | 57 | 50 | 45 | 66 | 56 | 49 | 45 | 55 | 49 | 45 | 54 | 48 | 45 | 53 | 48 | 44 | 43
[5 empty] | 52 | 10 | 64 | 53 | 46 | 41 | 63 | 52 | 46 | 41 | 51 | 45 | 41 | 50 | 45 | 41 | 50 | 44 | 41 | 39
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 314
Energy Density (W/m^2) = |  |  |  | 4.4444
Space to Height Ratio (SHR) = |  | (<1.5) |  | 1.2084
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95

## Highbay WB
Internal Lighting Calculation Sheet
Project name |  |  | Date : | 2013-10-17
Building name |  |  | Required Lux (E) = | 300
Room name
Room Index |  |  | Reflection Factors |  | ↓ Copy Column corresponding to reflectance values
Length (L) = | 9 | m
Width (W) = | 6 | m | Floor = | 20 | 20 | RF | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Height (H) = | 3 | m | Ceiling = | 70 | 70 | RC | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 30 | 30 | 30 | 10 | 10 | 10 | 0
Working level = | 0.85 | m | Wall = | 50 | 50 | RW | 70 | 50 | 30 | 10 | 70 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 50 | 30 | 10 | 0
Fixt. Level (Hf) = | 0 | m
Hm = H – Hf = | 2.15 | m |  |  | 116 | 0 | 119 | 119 | 119 | 119 | 116 | 116 | 116 | 116 | 111 | 111 | 111 | 106 | 106 | 106 | 102 | 102 | 102 | 100
Luminaire type : | 2x2 Panel Recessed |  | Lamp type : | LED | 106 | 1 | 111 | 108 | 105 | 102 | 109 | 106 | 103 | 100 | 101 | 99 | 97 | 98 | 96 | 94 | 94 | 93 | 91 | 89
|  |  | Lamp Wattage = | 30 | 95 | 2 | 104 | 97 | 92 | 87 | 101 | 95 | 90 | 86 | 92 | 88 | 84 | 89 | 85 | 82 | 86 | 83 | 81 | 79
|  |  | Lamp Flux = | 3000 | 86 | 3 | 96 | 87 | 81 | 76 | 94 | 86 | 80 | 75 | 83 | 78 | 74 | 81 | 76 | 72 | 78 | 74 | 71 | 69
Room Index (K ) = | 1.6744 |  |  |  | 78 | 4 | 89 | 79 | 72 | 66 | 87 | 78 | 71 | 66 | 75 | 69 | 65 | 73 | 68 | 64 | 71 | 67 | 63 | 61
Utilization F. (Uf) = | 0.95 |  | Maintenance Factor (Mf) = | 0.722 | 71 | 5 | 83 | 72 | 64 | 58 | 81 | 71 | 63 | 58 | 69 | 62 | 57 | 67 | 61 | 57 | 65 | 60 | 56 | 54
No. of Luminaries required (N) = |  |  | 7.8729 |  | 64 | 6 | 77 | 65 | 57 | 52 | 75 | 64 | 57 | 52 | 63 | 56 | 51 | 61 | 55 | 51 | 60 | 54 | 50 | 49
[5 empty] | 59 | 7 | 72 | 60 | 52 | 46 | 70 | 59 | 51 | 46 | 57 | 51 | 46 | 56 | 50 | 46 | 55 | 49 | 45 | 43
No. of Luminaries along length (Ng) = |  |  | 3.4365 | 4 | 54 | 8 | 67 | 55 | 47 | 42 | 65 | 54 | 47 | 42 | 53 | 46 | 41 | 51 | 45 | 41 | 50 | 45 | 41 | 39
No. of Luminaries along breadth (Nc) = |  |  | 2.291 | 2 | 50 | 9 | 62 | 50 | 43 | 38 | 61 | 50 | 42 | 38 | 49 | 42 | 37 | 48 | 42 | 37 | 47 | 41 | 37 | 35
[5 empty] | 46 | 10 | 59 | 46 | 39 | 34 | 57 | 46 | 39 | 34 | 45 | 38 | 34 | 44 | 38 | 34 | 43 | 38 | 34 | 32
Actual No. of Luminaires (Na)=Ng*Nc= |  |  |  | 8
Actual Lux (Lum) = |  |  |  | 305
Energy Density (W/m^2) = |  |  |  | 4.4444
Space to Height Ratio (SHR) = |  | (<1.5) |  | 1.2084
Note:
Lamp Lumen Depreciation (LLD) = |  |  | 0.8
(For replacement @ 80% light output level)
Luminaire Dirt Depreciation (LDD) = |  |  | 0.95
Room Surface Dirt Depreciation (RSDD) = |  |  | 0.95