## WELL to sump
SUMBERSIBLE PUMP SELECTION DATA SHEET
Project
| Head above ground | 15 | m
| Depth | 9 | m
| Total Head | 24 | m
| Distance to discharge point | 50 | m
| Discharge | 10 | Cu.m/Hr | 2.8 | Lps
| Pipe Dia for 1.5m/s fluid velocity | 48.7639 | mm | =sqrt(4*Q/(pi*velocity))
| Discharge pipe dia | 65 | mm
| Model | KOS-335+M
| Pump delivery pipe dia | 50 | mm
| Velocity discharge line | 0.84 | m/s
| Velocity delivery | 1.42 | m/s
| Velocity Head | 0 | m
|  |  |  | Kl | Hl
| No of bents/Tees etc. | 10 | Nos | 0.7 | 0.25 | m
| NRV Horiz | 1 | Nos | 2 | 0.07 | m
| Gate | 3 | Nos | 0.2 | 0.02 | m
| Butterfly Valve | 0 | Nos | 0.08 | 0 | m
| Entry, Exit etc. |  |  |  | 0.5 | m
[5 empty] | 0.8 | m
% of length
| Friction Head Loss discharge | 0.75 | 1.5%
| Friction Head Loss delivery | 0.5 | 5.6%
| Friction Head Loss Total | 1.25 | m
| Accessories Head Loss | 0.8 | m
| Total Head Loss | 2.05 | 3.5%
| Effective Head | 26.1 | m
| Estimated HP of Pump required | 1.9 | HP
PUMP DISCHARGE CALC
|  | Hour |  | Time Pumped |  | Day
1 | Seepage rate | 30 | Cu.m/Hr |  |  | 720 | Cu.m
2 | Pumpout | 10 | Cu.m/Hr | 2 | Hrs | 20 | Cu.m
3 | Available static column |  |  |  |  | 40 | Cu.m
| Safety Factor (Pumpout vs seepage) | 3 | (Minimum 2-3 for borewells or for continous pumping)
| Safety Factor (Pumpout vs available static column) |  | (>1.5 for open wells) |  |  | 2
HEAD LOSS PER LENGTH OF PIPE CALCULATION
|  | DISCHARGE | DELIVERY
| P | 1000 | 1000
| V | 0.84 | 1.42
| D | 0.065 | 0.05
| mu | 0.0008 | 0.0008
| e | 0.15 | 0.15 | Roughness 0.15 for GI, 0 for Plastic
| e_rel | 0.00231 | 0.003
| Re | 68250 | 88750
| f | 0.0264 | 0.0273
| hl | 0.015 | 0.056