## Calc
BATTERY SIZING SHEET
| UPS kVA | 30 | kVA
| PF | 0.8
| Efficiency | 90 | %
| Number of battery per string | 30
| Number of strings | 1
| Battery voltage | 12 | V
| Cell voltage | 2 | V
| Float cell voltage | 2.25 | V
| End cell voltage | 1.75 | V
| Derating factor | 1
Watts per cell method
| Required watts per cell | 148 | W/cell
| Required watts per battery | 888 | W/battery
Amperes per cell method
| Amperes per cell | 74 | A